## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | jospehine
[7 empty] | Month/Year: | 2024-07-01
System Name: | Morrison's Lodge |  |  | ID#: 4193508 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] |  | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.21
2 |  |  | 0.37 | 0.34
3 |  |  | 0.3
4 |  |  | 0.25
5 |  |  | 0.29
6 |  |  | 0.26
7 |  |  | 0.25
8 |  |  | 0.18
9 |  |  | 0.21
10 |  |  | 0.31
11 |  |  | 0.2
12 |  |  | 0.17
13 |  |  | 0.22
14 |  |  | 0.3
15 |  |  | 0.27
16 |  |  | 0.18
17 |  |  | 0.16
18 |  |  | 0.23
19 |  |  | 0.19
20 |  |  | 0.24
21 |  |  | 0.19
22 |  |  | 0.24
23 |  |  | 0.19
24 |  |  | 0.13
25 |  |  | 0.27
26 |  |  | 0.19
27 |  |  | 0.17
28 |  |  | 0.23
29 |  |  | 0.18
30 |  |  | 0.33
31 |  |  | 0.32
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | Trenton Douglas
[5 empty] | Trenton Douglas |  |  | 2024-08-05
[5 empty] | 5414799554 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Morrison's Lodge |  | ID#: 4193508 |  | 2024-07-01 |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.8 | 60 | 108 | 17.8 | 8.1 | 37.2004 | YES | 1.1
2 | 2 | 60 | 120 | 17.8 | 8.1 | 38.0538 | YES | 1.2
3 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 1.3
4 | 2 | 60 | 120 | 18.9 | 8.2 | 36.7018 | YES | 2.1
5 | 2 | 60 | 120 | 19.4 | 8.3 | 36.8372 | YES | 1.5
6 | 2 | 60 | 120 | 20.6 | 8.1 | 31.5859 | YES | 1.1
7 | 2 | 60 | 120 | 20.6 | 8.1 | 31.5859 | YES | 1.3
8 | 2 | 60 | 120 | 20.6 | 8.1 | 31.5859 | YES | 1.6
9 | 2 | 60 | 120 | 20.6 | 8.2 | 32.7769 | YES | 1
10 | 2 | 60 | 120 | 20 | 8.2 | 34.113 | YES | 1.7
11 | 2 | 60 | 120 | 20 | 8.2 | 34.113 | YES | 1.8
12 | 2 | 60 | 120 | 21.7 | 8.2 | 30.4589 | YES | 2
13 | 2 | 60 | 120 | 22.2 | 8.2 | 29.4588 | YES | 0.9
14 | 2 | 60 | 120 | 21.7 | 8.1 | 29.35 | YES | 2
15 | 2 | 60 | 120 | 21.7 | 8.1 | 29.35 | YES | 0.8
16 | 2 | 60 | 120 | 21.7 | 8.1 | 29.35 | YES | 1.2
17 | 1.8 | 60 | 108 | 21.7 | 8.1 | 28.6877 | YES | 2
18 | 2 | 60 | 120 | 20.6 | 8.2 | 32.7769 | YES | 1.1
19 | 2 | 60 | 120 | 21.7 | 8.2 | 30.4589 | YES | 1.2
20 | 2 | 60 | 120 | 21.1 | 8.1 | 30.5497 | YES | 2.3
21 | 2 | 60 | 120 | 21.7 | 8.1 | 29.35 | YES | 1.7
22 | 2 | 60 | 120 | 21.1 | 8.1 | 30.5497 | YES | 2.1
23 | 2 | 60 | 120 | 21.1 | 8.1 | 30.5497 | YES | 0.8
24 | 2 | 60 | 120 | 21.1 | 8.1 | 30.5497 | YES | 1.5
25 | 2 | 60 | 120 | 19.4 | 8.1 | 34.2144 | YES | 1.7
26 | 2 | 60 | 120 | 21.1 | 8.2 | 31.7027 | YES | 2
27 | 2 | 60 | 120 | 20 | 8.2 | 34.113 | YES | 3.2
28 | 2 | 60 | 120 | 20 | 8.2 | 34.113 | YES | 2.6
29 | 2 | 60 | 120 | 20 | 8.2 | 34.113 | YES | 1.8
30 | 2 | 60 | 120 | 20 | 8.1 | 32.8745 | YES | 1.1
31 | 2 | 60 | 120 | 20 | 8.2 | 34.113 | YES | 2.4
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2