## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Josephine
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-10-01
System Name: | Morrison's Lodge |  |  | ID#: 4193508 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.27
2 |  |  | 0.17
3 |  |  | 0.34
4 |  |  | 0.25
5 |  |  | 0.17
6 |  |  | 0.4
7 |  |  | 0.3
8 |  |  | 0.27
9 |  |  | 0.11
10 |  |  | 0.26
11 |  |  | 0.2
12 |  |  | 0.61
13 |  |  | 0.31
14 |  |  | 0.4
15 |  |  | 0.24
16 |  |  | 0.12
17 |  |  | 0.29
18 |  |  | 0.71
19 |  |  | 0.13
20 |  |  | 0.25
21 |  |  | 0.31
22 |  |  | 0.33
23 |  |  | 0.41
24 |  |  | 0.23
25 |  |  | 0.56
26 |  |  | 0.23
27 |  |  | 0.21
28 |  |  | 0.37
29 |  |  | 0.34
30 |  |  | 0.39
31 |  |  | 0.28
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Trenton Douglas
[5 empty] | Trenton Douglas |  |  | November 8 2024
[5 empty] | 5414799554 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | morrisons lodge |  | ID#: 41 |  | Month/Year: | 2024-10-24 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 1.8
2 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 1.5
3 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 1.6
4 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 1.6
5 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 2
6 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 1.5
7 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 1.4
8 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 2.1
9 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 3.3
10 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 3
11 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 0.9
12 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 3
13 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 2.9
14 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 3.3
15 | 2 | 60 | 120 | 17.8 | 8.2 | 39.4826 | YES | 2
16 | 2 | 60 | 120 | 16.8 | 8.2 | 42.189 | YES | 3
17 | 2 | 60 | 120 | 16 | 8.2 | 44.4845 | YES | 1.7
18 | 2 | 60 | 120 | 16.8 | 8.3 | 43.7699 | YES | 3.5
19 | 2 | 60 | 120 | 14.6 | 8.3 | 50.6241 | YES | 1.5
20 | 2 | 60 | 120 | 14.6 | 8.3 | 50.6241 | YES | 1.5
21 | 2 | 60 | 120 | 18 | 8.3 | 40.4244 | YES | 2.3
22 | 2 | 60 | 120 | 15.7 | 8.3 | 47.0745 | YES | 1.2
23 | 2 | 60 | 120 | 16.8 | 8.3 | 43.7699 | YES | 2.3
24 | 2 | 60 | 120 | 14.1 | 8.3 | 52.3234 | YES | 1.8
25 | 2 | 60 | 120 | 14.8 | 8.3 | 49.9597 | YES | 1.3
26 | 2 | 60 | 120 | 14.9 | 8.3 | 49.6307 | YES | 2
27 | 2 | 60 | 120 | 15 | 8.3 | 49.3039 | YES | 1.9
28 | 2 | 60 | 120 | 14.8 | 8.3 | 49.9597 | YES | 4
29 | 2 | 60 | 120 | 14.6 | 8.3 | 50.6241 | YES | 3
30 | 2 | 60 | 120 | 14.8 | 8.3 | 49.9597 | YES | 2
31 | 2 | 60 | 120 | 14.8 | 8.3 | 49.9597 | YES | 2.1
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2