## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Douglas
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-05-01
System Name: | Whistlers Bend |  |  | ID#: 41 93944 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | Well | Use | Only | 35
2 | Well | Use | Only | 35
3 | Well | Use | Only | 35
4 | Well | Use | Only | 35
5 | Well | Use | Only | 35
6 | Well | Use | Only | 35
7 | Well | Use | Only | 35
8 | Well | Use | Only | 35
9 | Well | Use | Only | 35
10 | 122 | 117 | 5 | 35 | 1.28
11 | 123 | 117 | 6 | 35 | 1.24
12 | 123 | 118 | 5 | 35 | 0.72
13 | 132 | 125 | 7 | 35 | 0.42
14 | 141 | 137 | 4 | 35 | 0.71
15 | 152 | 148 | 4 | 35 | 0.41
16 | 148 | 141 | 7 | 35 | 0.22
17 | 122 | 118 | 4 | 35 | 0.07
18 | 122 | 117 | 5 | 35 | 0.03
19 | 123 | 119 | 4 | 35 | 0.07
20 | 122 | 118 | 4 | 35 | 0.18
21 | 151 | 148 | 3 | 35 | 0.24
22 | 124 | 120 | 4 | 35 | 0.07
23 | 124 | 121 | 3 | 35 | 0.07
24 | 126 | 122 | 4 | 35 | 0.02
25 | 127 | 122 | 5 | 35 | 0.06
26 | 128 | 123 | 5 | 35 | 0.13
27 | 130 | 127 | 3 | 35 | 0.02
28 | 134 | 127 | 7 | 35 | 0.04
29 | 136 | 131 | 5 | 35 | 0.05
30 | 128 | 124 | 4 | 35 | 0.07
31 | 130 | 127 | 2 | 35 | 1.18
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | Josh Templeton
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:5-10-2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 )643 0638 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whistlers Bend |  | ID#: 41 | 93944 | Month/Year: | 2021-05-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | well only | 41 | #VALUE! | well only | well only | #VALUE! | #VALUE!
2 | well only | 41 | #VALUE! | well only | well only | #VALUE! | #VALUE!
3 | well only | 41 | #VALUE! | well only | well only | #VALUE! | #VALUE!
4 | well only | 41 | #VALUE! | well only | well only | #VALUE! | #VALUE!
5 | well only | 41 | #VALUE! | well only | well only | #VALUE! | #VALUE!
6 | well only | 41 | #VALUE! | well only | well only | #VALUE! | #VALUE!
7 | well only | 41 | #VALUE! | well only | well only | #VALUE! | #VALUE!
8 | well only | 41 | #VALUE! | well only | well only | #VALUE! | #VALUE!
9 | well only | 41 | #VALUE! | well only | well only | #VALUE! | #VALUE!
10 | 1.6 | 41 | 65.6 | 18.8 | 8.9 | 22.8459 | YES
11 | 0.7 | 41 | 28.7 | 18.9 | 8.8 | 19.7574 | YES
12 | 1.8 | 41 | 73.8 | 17.1 | 7 | 12.9654 | YES
13 | 1.9 | 41 | 77.9 | 17.8 | 7.4 | 14.5204 | YES
14 | 2 | 41 | 82 | 17.4 | 7.2 | 14.0055 | YES
15 | 2.1 | 41 | 86.1 | 17.7 | 7.8 | 17.3417 | YES
16 | 2.1 | 41 | 86.1 | 16.8 | 7.5 | 16.4794 | YES
17 | 2.2 | 41 | 90.2 | 17.4 | 8.1 | 19.9866 | YES
18 | 2.4 | 41 | 98.4 | 17.8 | 7.2 | 14.2732 | YES
19 | 2.4 | 41 | 98.4 | 17.1 | 7.2 | 14.9566 | YES
20 | 2.2 | 41 | 90.2 | 17.3 | 7.6 | 16.7295 | YES
21 | 2.1 | 41 | 86.1 | 17.8 | 7.7 | 16.6014 | YES
22 | 2.2 | 41 | 90.2 | 17.7 | 8.1 | 19.5928 | YES
23 | 1.9 | 41 | 77.9 | 17.9 | 7.2 | 13.3906 | YES
24 | 2.3 | 41 | 94.3 | 18.2 | 7.4 | 14.7977 | YES
25 | 2.1 | 41 | 86.1 | 16.1 | 7.3 | 16.0345 | YES
26 | 2.1 | 41 | 86.1 | 15.7 | 7.4 | 17.0879 | YES
27 | 1.9 | 41 | 77.9 | 15.3 | 7.2 | 15.9312 | YES
28 | 2.1 | 41 | 86.1 | 15.2 | 7.4 | 17.6659 | YES
29 | 2.2 | 41 | 90.2 | 16.4 | 7.2 | 15.3188 | YES
30 | 2.2 | 41 | 90.2 | 16.8 | 7.6 | 17.2956 | YES
31 | 2.3 | 41 | 94.3 | 18.1 | 8.3 | 20.7723 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2