## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Douglas
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-08-01
System Name: | Whistlers Bend |  |  | ID#: 41 93944 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 121 | 133 | 12 | 35 | 0.21
2 | 122 | 130 | 8 | 35 | 0.33
3 | 121 | 131 | 10 | 35 | 0.28
4 | 122 | 131 | 9 | 35 | 0.38
5 | 125 | 132 | 7 | 35 | 0.36
6 | 116 | 132 | 6 | 35 | 0.28
7 | 125 | 139 | 14 | 35 | 0.41
8 | 118 | 123 | 5 | 35 | 0.49
9 | 118 | 122 | 4 | 35 | 0.72
10 | 119 | 124 | 5 | 35 | 0.52
11 | 120 | 123 | 3 | 35 | 0.46
12 | 121 | 122 | 1 | 35 | 0.49
13 | 119 | 124 | 5 | 35 | 0.37
14 | 118 | 123 | 5 | 35 | 0.28
15 | 121 | 126 | 5 | 35 | 0.18
16 | 120 | 126 | 6 | 35 | 0.21
17 | 119 | 127 | 8 | 35 | 0.33
18 | 121 | 126 | 5 | 35 | 0.38
19 | 120 | 126 | 6 | 35 | 0.32
20 | 123 | 127 | 5 | 35 | 0.41
21 | 122 | 129 | 7 | 35 | 0.35
22 | 123 | 131 | 8 | 35 | 0.55 | .
23 | 122 | 130 | 8 | 35 | 0.51
24 | 124 | 133 | 9 | 35 | 0.41
25 | 125 | 133 | 8 | 35 | 0.34
26 | 125 | 134 | 9 | 35 | 0.55
27 | 118 | 124 | 6 | 35 | 0.44
28 | 118 | 125 | 7 | 35 | 0.38
29 | 119 | 124 | 5 | 35 | 0.21
30 | 118 | 124 | 6 | 35 | 0.28
31 | 119 | 125 | 6 | 35 | 0.26
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | Josh Templeton
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:9/9/21
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 )643 0638 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whistlers Bend |  | ID#: 41 | 93944 | Month/Year: | 2021-05-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.1 | 41 | 45.1 | 23.4 | 7.8 | 10.5587 | YES
2 | 1 | 41 | 41 | 23.5 | 7.8 | 10.3674 | YES
3 | 1.4 | 41 | 57.4 | 22.7 | 7.74 | 11.2036 | YES
4 | 1.1 | 41 | 45.1 | 23.5 | 7.9 | 10.8882 | YES
5 | 1.3 | 41 | 53.3 | 22.2 | 7.85 | 11.9353 | YES
6 | 1.4 | 41 | 57.4 | 23.5 | 8.2 | 12.6065 | YES
7 | 1 | 41 | 41 | 23.1 | 7.9 | 11.0578 | YES
8 | 0.9 | 41 | 36.9 | 23.2 | 8.14 | 11.8773 | YES
9 | 1.2 | 41 | 49.2 | 22.9 | 7.94 | 11.6413 | YES
10 | 1.2 | 41 | 49.2 | 23.4 | 7.99 | 11.4684 | YES
11 | 1.4 | 41 | 57.4 | 23.2 | 8.3 | 13.3506 | YES
12 | 1.2 | 41 | 49.2 | 23.1 | 8.25 | 12.894 | YES
13 | 1.3 | 41 | 53.3 | 22.8 | 8.24 | 13.258 | YES
14 | 1 | 41 | 41 | 23.5 | 8.21 | 12.0864 | YES
15 | 1.1 | 41 | 45.1 | 23.4 | 8.09 | 11.7691 | YES
16 | 1.3 | 41 | 53.3 | 23.5 | 8.22 | 12.5561 | YES
17 | 1.1 | 41 | 45.1 | 23.2 | 7.89 | 11.0691 | YES
18 | 1.2 | 41 | 49.2 | 23.3 | 7.95 | 11.3745 | YES
19 | 1.2 | 41 | 49.2 | 23.3 | 8.12 | 12.1203 | YES
20 | 1.4 | 41 | 57.4 | 22.9 | 8.16 | 12.9301 | YES
21 | 1.7 | 41 | 69.7 | 22.8 | 8.3 | 14.1912 | YES
22 | 1.3 | 41 | 53.3 | 23.1 | 8.16 | 12.6125 | YES
23 | 1.3 | 41 | 53.3 | 23.2 | 8.18 | 12.6219 | YES
24 | 1.5 | 41 | 61.5 | 23.1 | 8.34 | 13.7986 | YES
25 | 1.2 | 41 | 49.2 | 23.2 | 8.24 | 12.7602 | YES
26 | 1.1 | 41 | 45.1 | 23.4 | 8.05 | 11.5945 | YES
27 | 1.2 | 41 | 49.2 | 23.4 | 8.1 | 11.9495 | YES
28 | 1.4 | 41 | 57.4 | 23.2 | 7.9 | 11.5007 | YES
29 | 1.4 | 41 | 57.4 | 23.3 | 7.96 | 11.6826 | YES
30 | 1.2 | 41 | 49.2 | 23.2 | 8.15 | 12.3393 | YES
31 | 1.3 | 41 | 53.3 | 23.4 | 8.1 | 12.0875 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2