## Table 1
OHA - Drinking Water Services – Turbidity Monitoring Report Form Cartridge or Bag Filtration | [10 empty] | County: Month/Year: |  | Jackson
2021-08-01
| System Name: Latgawa Methodist Church Camp |  |  |  |  | ID# 41-93973 |  |  |  |  | WTP ID:
| DAY | PSI Before Filter | PSI After Filter |  | PSID |  | PSID When to Change Filter |  | Daily Turbidity Reading [NTU] |  |  | Highest Reading of the Day 1 [NTU]
| 1 | 65 | 62 |  | 3 |  | 25 |  | 0.01 |  |  | 0.01
| 2 | 65 | 63 |  | 2 |  | 25 |  | 0.01 |  |  | 0.01
| 3 | 64 | 63 |  | 1 |  | 25 |  | 0.01 |  |  | 0.01
| 4 | 64 | 62 |  | 2 |  | 25 |  | 0.02 |  |  | 0.02
| 5 | 64 | 62 |  | 2 |  | 25 |  | 0.02 |  |  | 0.02
| 6 | 65 | 62 |  | 3 |  | 25 |  | 0.02 |  |  | 0.02
| 7 | 65 | 63 |  | 2 |  | 25 |  | 0.02 |  |  | 0.02
| 8 | 64 | 61 |  | 3 |  | 25 |  | 0.02 |  |  | 0.02
| 9 | 63 | 61 |  | 2 |  | 25 |  | 0.02 |  |  | 0.02
| 10 | 63 | 60 |  | 3 |  | 25 |  | 0.02 |  |  | 0.02
| 11 | 63 | 60 |  | 3 |  | 25 |  | 0.02 |  |  | 0.02
| 12 | 63 | 59 |  | 4 |  | 25 |  | 0.02 |  |  | 0.02
| 13 | 64 | 60 |  | 4 |  | 25 |  | 0.02 |  |  | 0.02
| 14 | 63 | 60 |  | 3 |  | 25 |  | 0.02 |  |  | 0.02
| 15 | 64 | 61 |  | 3 |  | 25 |  | 0.01 |  |  | 0.01
| 16 | 64 | 60 |  | 4 |  | 25 |  | 0.01 |  |  | 0.01
| 17 | 65 | 61 |  | 4 |  | 25 |  | 0.01 |  |  | 0.01
| 18 | 65 | 62 |  | 3 |  | 25 |  | 0.01 |  |  | 0.01
| 19 | 64 | 62 |  | 2 |  | 25 |  | 0.02 |  |  | 0.02
| 20 | 65 | 62 |  | 3 |  | 25 |  | 0.03 |  |  | 0.03
| 21 | 65 | 61 |  | 4 |  | 25 |  | 0.03 |  |  | 0.03
| 22 | 66 | 61 |  | 5 |  | 25 |  | 0.03 |  |  | 0.03
| 23 | 65 | 62 |  | 3 |  | 25 |  | 0.03 |  |  | 0.03
| 24 | 65 | 62 |  | 3 |  | 25 |  | 0.03 |  |  | 0.03
| 25 | 64 | 63 |  | 1 |  | 25 |  | 0.03 |  |  | 0.03
| 26 | 64 | 62 |  | 2 |  | 25 |  | 0.03 |  |  | 0.03
| 27 | 64 | 63 |  | 1 |  | 25 |  | 0.03 |  |  | 0.03
| 28 | 64 | 62 |  | 2 |  | 25 |  | 0.03 |  |  | 0.03
| 29 | 64 | 61 |  | 3 |  | 25 |  | 0.03 |  |  | 0.03
| 30 | 65 | 63 |  | 2 |  | 25 |  | 0.03 |  |  | 0.03
| 31 | 64 | 62 |  | 2 |  | 25 |  | 0.03 |  |  | 0.03
Cartridge Filtration Monthly Summary | [5 empty] | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No |  | CT's met everyday? (see back) Yes / No |  |  |  | All Cl2 residual at entry point ≥ 0.2 mg/l? Yes / No
Notes: PSI = pounds per square inch PSID = pounds per square inch difference (before filter – after filter) PSID When to Change Filter = Manufacturer’s recommendation; may need to look in manual for manufacturer’s specifications when to change the filter, at what PSID. | [5 empty] | PRINTED NAME: Kate Vaden
[6 empty] | SIGNATURE: | [5 empty] | DATE: 9/2/21
[6 empty] | PHONE #: (541)531-6326 | [5 empty] | CERT #:
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in “Daily Turbidity Reading” Column may not correspond to continuous readings’ maximum. PAGE 1 of 2
OHA - Drinking Water Services – Surface Water Quality Data Form | [8 empty] | Month/Year: September 2021
| System Name: |  |  |  |  | ID# 41 |  | WTP
| Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time ( T ) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
|  | [ppm or mg/L] | [minutes] | C X T | [° C] |  | Use tables | Yes / No | [GPM]
| 1 / | 1.8 | 125 | 225 | 25.9 | 7.9 | 20 | Yes | 15
| 2 / | 1.6 | 125 | 200 | 24.6 | 8.1 | 35 | Yes | 15
| 3 / | 1.8 | 125 | 225 | 24.8 | 8.2 | 36 | Yes | 15
| 4 / | 1.4 | 125 | 175 | 25.2 | 8.1 | 23 | Yes | 15
| 5 / | 1.2 | 125 | 150 | 25.8 | 8.4 | 22 | Yes | 15
| 6 / | 1.4 | 125 | 175 | 26 | 7.8 | 19 | Yes | 15
| 7 / | 1 | 125 | 125 | 26.1 | 8.2 | 22 | Yes | 15
| 8 / | 1.2 | 125 | 150 | 25.4 | 8.1 | 22 | Yes | 15
| 9 / | 1.6 | 125 | 200 | 24.3 | 8.4 | 35 | Yes | 15
| 10 / | 1.4 | 125 | 175 | 28.7 | 8.6 | 27 | Yes | 15
| 11 / | 2 | 125 | 250 | 27.5 | 8.4 | 25 | Yes | 15
| 12 / | 1.2 | 125 | 150 | 26.1 | 8.1 | 22 | Yes | 15
| 13 / | 0.8 | 125 | 100 | 25.3 | 8.3 | 21 | Yes | 15
| 14 / | 0.8 | 125 | 100 | 24.1 | 8.7 | 38 | Yes | 15
| 15 / | 1.4 | 125 | 175 | 22.3 | 8.6 | 41 | Yes | 15
| 16 / | 1 | 125 | 125 | 25.1 | 8.2 | 22 | Yes | 15
| 17 / | 0.6 | 125 | 75 | 26.7 | 7.9 | 27 | Yes | 15
| 18 / | 1 | 125 | 125 | 28.1 | 8 | 18 | Yes | 15
| 19 / | 1.8 | 125 | 225 | 29.2 | 8.5 | 24 | Yes | 15
| 20 / | 1.2 | 125 | 150 | 27.9 | 8.4 | 22 | Yes | 15
| 21 / | 2.2 | 125 | 275 | 26.4 | 8.3 | 25 | Yes | 15
| 22 / | 1.4 | 125 | 175 | 28.2 | 8.7 | 27 | Yes | 15
| 23 / | 1.8 | 125 | 225 | 23.1 | 7.6 | 30 | Yes | 15
| 24 / | 1.8 | 125 | 225 | 21.5 | 7.7 | 30 | Yes | 15
| 25 / | 0.8 | 125 | 100 | 19.3 | 7.6 | 35 | Yes | 15
| 26 / | 1.2 | 125 | 150 | 16.7 | 7.8 | 37 | Yes | 15
| 27 / | 1.6 | 125 | 200 | 18.2 | 7.4 | 32 | Yes | 15
| 28 / | 1 | 125 | 125 | 15.6 | 7.6 | 36 | Yes | 15
| 29 / | 1.8 | 125 | 225 | 15 | 7.9 | 40 | Yes | 15
| 30 / | 2 | 125 | 250 | 14.8 | 7.7 | 61 | Yes | 15
| 31 / | 1.4 | 125 | 175 | 15.4 | 7.5 | 31 | Yes | 15
2 If Cl2 at entry point < 0.2 mg/l, OR CT not met, notify DWS within 24 hours. Revised August 2016 Download form at: public.health.oregon.gov/HealthyEnvironments/DrinkingWater/Monitoring/Documents/turb-cartridge.pdf Return by 10th of following month by email, fax or mail to: dwp.dmce@state.or.us; Fax 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350