## Turbidity and CT - Table 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-06-01
System Name: | Woahink Lake Suites |  |  | ID#: 4194188 |  | WTP ID: WTP-A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 5 |  | 0.55
2 |  |  | 5 |  | 0.58
3 |  |  | 5 |  | 0.65
4 |  |  | 5 |  | 0.69
5 |  |  | 5 |  | 0.77
6 |  |  | 5 |  | 0.56
7 |  |  | 5 |  | 0.61
8 |  |  | 5 |  | 0.67
9 |  |  | 5 |  | 0.52
10 |  |  | 5 |  | 0.57
11 |  |  | 6 |  | 0.91
12 |  |  | 6 |  | 0.86
13 |  |  | 6 |  | 0.71
14 |  |  | 6 |  | 0.79
15 |  |  | 6 |  | 0.66
16 |  |  | 6 |  | 0.63
17 |  |  | 6 |  | 0.55
18 |  |  | 6 |  | 0.48
19 |  |  | 6 |  | 0.42
20 |  |  | 6 |  | 0.57
21 |  |  | 6 |  | 0.58
22 |  |  | 6 |  | 0.68
23 |  |  | 6 |  | 0.64
24 |  |  | 6 |  | 0.67
25 |  |  | 6 |  | 0.53
26 |  |  | 6 |  | 0.44
27 |  |  | 6 |  | 0.52
28 |  |  | 6 |  | 0.63
29 |  |  | 6 |  | 0.68
30 |  |  | 6 |  | 0.6
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Dan Reitz
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:06/06/2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 342-1718 |  | CERT #: D&T 6528
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Woahink Lake Suites |  | ID#: 4194188 |  | Month/Year: | 2022-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.55 | 100 | 55 | 16.1 | 5.66 | 14.5003 | Yes
2 | 0.52 | 100 | 52 | 15.9 | 6.2 | 17.9779 | Yes
3 | 0.6 | 100 | 60 | 16.4 | 6.3 | 18.2139 | Yes
4 | 2 | 100 | 200 | 16.3 | 5.48 | 15.8253 | Yes
5 | 1.56 | 100 | 156 | 16.7 | 5.4 | 14.1858 | Yes
6 | 1.21 | 100 | 121 | 16.9 | 5.5 | 13.9513 | Yes
7 | 0.53 | 100 | 53 | 17 | 5.6 | 13.2891 | Yes
8 | 0.5 | 100 | 50 | 17.9 | 5.5 | 11.9733 | Yes
9 | 1.16 | 100 | 116 | 18.5 | 5.69 | 13.3587 | Yes
10 | 1.11 | 100 | 111 | 18.5 | 5.43 | 12.0173 | Yes
11 | 0.76 | 100 | 76 | 18.8 | 5.45 | 11.3776 | Yes
12 | 1 | 100 | 100 | 17.8 | 5.6 | 13.2915 | Yes
13 | 0.96 | 100 | 96 | 17.8 | 6.5 | 18.6209 | Yes
14 | 0.95 | 100 | 95 | 18.5 | 6.3 | 16.4435 | Yes
15 | 0.87 | 100 | 87 | 18.8 | 6.4 | 16.5772 | Yes
16 | 0.5 | 100 | 50 | 17.9 | 6.5 | 17.5337 | Yes
17 | 0.52 | 100 | 52 | 19.4 | 6.2 | 14.1537 | Yes
18 | 0.7 | 100 | 70 | 19 | 5.6 | 11.8055 | Yes
19 | 1.25 | 100 | 125 | 17.7778 | 5.8 | 14.797 | Yes
20 | 0.99 | 100 | 99 | 18.5 | 5.8 | 13.6572 | Yes
21 | 0.87 | 100 | 87 | 18.3 | 5.7 | 13.1395 | Yes
22 | 0.77 | 100 | 77 | 19.4 | 5.56 | 11.3999 | Yes
23 | 1.23 | 100 | 123 | 19.1 | 5.4 | 11.5572 | Yes
24 | 0.73 | 100 | 73 | 18.9 | 5.5 | 11.4783 | Yes
25 | 1.15 | 100 | 115 | 19.3 | 5.5 | 11.7344 | Yes
26 | 0.91 | 100 | 91 | 19.3 | 5.6 | 11.8537 | Yes
27 | 0.5 | 100 | 50 | 19.4 | 5.7 | 11.6537 | Yes
28 | 0.51 | 100 | 51 | 19 | 5.9 | 12.9557 | Yes
29 | 1.02 | 100 | 102 | 19.3 | 5.6 | 12.0094 | Yes
30 | 1.09 | 100 | 109 | 19.1 | 5.6 | 12.2785 | Yes
2 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | [6 empty] | Revised February 2012
PAGE 2 of 2

## Temp F to C
DAY | Farenheit | Celcius | Celcius | Farenheit
1 | 57 | 13.8889 |  | 32
2 | 58.1 | 14.5 |  | 32
3 | 56.7 | 13.7222 |  | 32
4 | 59 | 15 |  | 32
5 | 55.8 | 13.2222 |  | 32
6 | 55.7 | 13.1667 |  | 32
7 | 59.6 | 15.3333 |  | 32
8 | 57 | 13.8889 |  | 32
9 | 58.8 | 14.8889 |  | 32
10 | 55.7 | 13.1667 |  | 32
11 | 57.1 | 13.9444 |  | 32
12 | 57.9 | 14.3889 |  | 32
13 | 59.3 | 15.1667 |  | 32
14 | 58.5 | 14.7222 |  | 32
15 | 59 | 15 |  | 32
16 | 61.2 | 16.2222 |  | 32
17 | 61.9 | 16.6111 |  | 32
18 | 61.3 | 16.2778 |  | 32
19 | 64 | 17.7778 |  | 32
20 | 63.3 | 17.3889 |  | 32
21 | 62.9 | 17.1667 |  | 32
22 | 60.8 | 16 |  | 32
23 | 61.9 | 16.6111 |  | 32
24 | 60.3 | 15.7222 |  | 32
25 | 61.6 | 16.4444 |  | 32
26 | 61.4 | 16.3333 |  | 32
27 | 60.8 | 16 |  | 32
28 | 61.7 | 16.5 |  | 32
29 | 60.9 | 16.0556 |  | 32
30 | 60.7 | 15.9444 |  | 32
31 | 61 | 16.1111 |  | 32