## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clackamas
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-05-01
System Name: | Butte Creek Scout Ranch |  |  | ID#: 41 | 94191 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.1
2 |  |  |  |  | 0.1
3 |  |  |  |  | 0.09
4 |  |  |  |  | 0.08
5 |  |  |  |  | .09+
6 |  |  |  |  | 0.1
7 |  |  |  |  | 0.09
8 |  |  |  |  | 0.09
9 |  |  |  |  | 0.09
10 |  |  |  |  | 0.09
11 |  |  |  |  | 0.08
12 |  |  |  |  | 0.08
13 |  |  |  |  | 0.08
14 |  |  |  |  | 0.08
15 |  |  |  |  | 0.08
16 |  |  |  |  | 0.08
17 |  |  |  |  | 0.08
18 |  |  |  |  | 0.08
19 |  |  |  |  | 0.08
20 |  |  |  |  | 0.08
21 |  |  |  |  | 0.09
22 |  |  |  |  | 0.09
23 |  |  |  |  | 0.08
24 |  |  |  |  | 0.09
25 |  |  |  |  | 0.09
26 |  |  |  |  | 0.08
27 |  |  |  |  | 0.09
28 |  |  |  |  | 0.09
29 |  |  |  |  | 0.08
30 |  |  |  |  | 0.08
31 |  |  |  |  | 0.07
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Bill Hood
[5 empty] | SIGNATURE: |  |  | DATE: 6/9/25
[5 empty] | PHONE #: ( 503)539-3834 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Butte Creek Scout Ranch |  | ID#: 41 | 94191 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.55 | 280 | 154 | 11.3 | 7.1 | 34.9443 | YES | 1.9
2 | 0.56 | 280 | 156.8 | 11.1 | 7.1 | 35.4348 | YES | 3
3 | 0.55 | 280 | 154 | 11.2 | 7.1 | 35.1692 | YES | 4.7
4 | 0.5 | 280 | 140 | 11.4 | 7.1 | 34.531 | YES | 2.9
5 | 0.5 | 280 | 140 | 11.4 | 6.7 | 30.1658 | YES | 2.1
6 | 0.5 | 280 | 140 | 11.7 | 7 | 32.7441 | YES | 1.6
7 | 0.5 | 280 | 140 | 11.4 | 7 | 33.3752 | YES | 1.6
8 | 0.5 | 280 | 140 | 11.5 | 7 | 33.1633 | YES | 1.6
9 | 0.5 | 280 | 140 | 10.8 | 7.2 | 37.1427 | YES | 1.6
10 | 0.5 | 280 | 140 | 11.3 | 7.1 | 34.7529 | YES | 1.9
11 | 0.5 | 280 | 140 | 12.3 | 7.1 | 32.6047 | YES | 2
12 | 0.5 | 280 | 140 | 12.1 | 7.2 | 34.1637 | YES | 2.1
13 | 0.5 | 280 | 140 | 11.9 | 7 | 32.3309 | YES | 1.9
14 | 0.55 | 280 | 154 | 12 | 7 | 32.3014 | YES | 2
15 | 0.5 | 280 | 140 | 11.8 | 7.2 | 34.8263 | YES | 1.8
16 | 0.5 | 280 | 140 | 11.1 | 6.9 | 32.8841 | YES | 1.8
17 | 0.5 | 280 | 140 | 12.2 | 7.1 | 32.8126 | YES | 2
18 | 0.5 | 280 | 140 | 11.6 | 7.2 | 35.2761 | YES | 1.9
19 | 0.5 | 280 | 140 | 11.7 | 7 | 32.7441 | YES | 1.8
20 | 0.49 | 280 | 137.2 | 11.5 | 7.2 | 35.4645 | YES | 2.1
21 | 0.46 | 280 | 128.8 | 11.4 | 7.1 | 34.3799 | YES | 2.1
22 | 0.44 | 280 | 123.2 | 11.9 | 7 | 32.121 | YES | 1.8
23 | 0.43 | 280 | 120.4 | 12 | 7.2 | 34.1203 | YES | 2.1
24 | 0.44 | 280 | 123.2 | 11.5 | 7.2 | 35.2699 | YES | 2.1
25 | 0.48 | 280 | 134.4 | 12 | 7 | 32.0569 | YES | 1.8
26 | 0.48 | 280 | 134.4 | 12.4 | 7.2 | 33.4423 | YES | 2.1
27 | 0.51 | 280 | 142.8 | 11.4 | 7.2 | 35.772 | YES | 1.9
28 | 0.52 | 280 | 145.6 | 11.9 | 7.1 | 33.5184 | YES | 10.4
29 | 0.65 | 280 | 182 | 12.3 | 7.1 | 33.1416 | YES | 7.2
30 | 0.58 | 280 | 162.4 | 13.7 | 7.1 | 29.3917 | YES | 3.1
31 | 0.54 | 280 | 151.2 | 13.7 | 7.1 | 29.2578 | YES | 4
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2