## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | C00S
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-01-21
System Name: | SLEEPY HOLLOW RV PARK |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 19 | 10 | 9 |  | 1.34
2 | 20 | 10 | 10 |  | 1.23
3 | 19 | 10 | 9 |  | 1.59
4 | 18 | 8 | 10 |  | 1.3
5 | 20 | 10 | 10 |  | 1.2
6 | 19 | 9 | 10 |  | 0.99
7 | 21 | 10 | 11 |  | 1.3
8 | 19 | 9 | 10 |  | 0.97
9 | 20 | 10 | 10 |  | 1.45
10 | 21 | 10 | 11 |  | 1.34
11 | 17 | 8 | 9 |  | 1.56
12 | 18 | 8 | 10 |  | 1.46
13 | 19 | 8 | 11 |  | 0.99
14 | 20 | 10 | 10 |  | 1.5
15 | 25 | 14 | 11 |  | 1.23
16 | 16 | 7 | 9 |  | 1.45
17 | 19 | 9 | 10 |  | 0.99
18 | 20 | 10 | 10 |  | 0.98
19 | 25 | 15 | 10 |  | 0.97
20 | 20 | 10 | 10 |  | 1.34
21 | 19 | 9 | 10 |  | 1.2
22 | 18 | 9 | 9 |  | 1.26
23 | 20 | 10 | 10 |  | 1.6
24 | 21 | 11 | 10 |  | 0.99
25 | 19 | 9 | 10 |  | 1.33
26 | 18 | 9 | 9 |  | 1.3
27 | 20 | 10 | 10 |  | 1.43
28 | 18 | 7 | 11 |  | 1.3
29 | 17 | 8 | 9 |  | 0.99
30 | 20 | 10 | 10 |  | 1.11
31 | 19 | 8 | 11 |  | 1.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Jesse Reigard
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Jesse Reigard |  | 2021-02-10
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541 ) 572-5494 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | SLEEPY HOLLOW |  | ID# 4194283 |  | Month/Year: | 2021-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2 | 28 | 56 | 16.5 | 6.9 | 26.6106 | YES
2 | 1.5 | 28 | 42 | 15.6 | 7.2 | 29.8396 | YES
3 | 1.5 | 28 | 42 | 15.4 | 7.1 | 29.1396 | YES
4 | 3 | 28 | 84 | 14.7 | 6.7 | 31.2346 | YES
5 | 3 | 28 | 84 | 15.3 | 6.3 | 25.864 | YES
6 | 1.5 | 28 | 42 | 15.6 | 6.5 | 22.9942 | YES
7 | 2 | 28 | 56 | 14.9 | 7.4 | 35.6367 | YES
8 | 2 | 28 | 56 | 15.5 | 7.2 | 31.8004 | YES
9 | 1.5 | 28 | 42 | 15.8 | 7.4 | 31.7092 | YES
10 | 1.5 | 28 | 42 | 14.7 | 7.1 | 30.534 | YES
11 | 2 | 28 | 56 | 14.3 | 7 | 31.9901 | YES
12 | 2 | 28 | 56 | 13.9 | 6.9 | 31.6605 | YES
13 | 1.5 | 28 | 42 | 14.2 | 6.3 | 23.4461 | YES
14 | 1.5 | 28 | 42 | 15.1 | 6.7 | 25.6223 | YES
15 | 3 | 28 | 84 | 15.7 | 7.2 | 35.1587 | YES
16 | 3 | 28 | 84 | 15.9 | 7.4 | 37.3527 | YES
17 | 1.5 | 28 | 42 | 16.2 | 6.7 | 23.798 | YES
18 | 2 | 28 | 56 | 16.6 | 6.3 | 21.1262 | YES
19 | 2 | 28 | 56 | 15.9 | 7.5 | 34.5983 | YES
20 | 1.5 | 28 | 42 | 15.4 | 7.3 | 31.3824 | YES
21 | 2 | 28 | 56 | 15.8 | 7 | 28.9425 | YES
22 | 1.5 | 28 | 42 | 16.1 | 6.7 | 23.9585 | YES
23 | 3 | 28 | 84 | 15.7 | 6.5 | 27.1255 | YES
24 | 1.5 | 28 | 42 | 16.5 | 7.2 | 28.0977 | YES
25 | 1.5 | 28 | 42 | 15.8 | 7.1 | 28.3708 | YES
26 | 3 | 28 | 84 | 15.5 | 6.4 | 26.4875 | YES
27 | 2 | 28 | 56 | 15.9 | 6.7 | 25.715 | YES
28 | 2 | 28 | 56 | 16.3 | 5.9 | 18.5499 | YES
29 | 1.5 | 28 | 42 | 16.1 | 6.2 | 19.867 | YES
30 | 2 | 28 | 56 | 15.9 | 6.6 | 24.7743 | YES
31 | 2 | 28 | 56 | 16.4 | 7.2 | 29.9471 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2