## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | C00S
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-08-01
System Name: | SLEEPY HOLLOW RV PARK |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 | 8 | 10 |  | 0.56
2 | 21 | 11 | 10 |  | 0.59
3 | 18 | 8 | 10 |  | 0.64
4 | 20 | 10 | 10 |  | 0.62
5 | 21 | 11 | 10 |  | 0.77
6 | 20 | 10 | 10 |  | 0.87
7 | 15 | 5 | 10 |  | 0.81
8 | 17 | 7 | 10 |  | 0.78
9 | 25 | 15 | 10 |  | 0.85
10 | 20 | 10 | 10 |  | 0.89
11 | 18 | 8 | 10 |  | 0.9
12 | 19 | 9 | 10 |  | 0.77
13 | 21 | 11 | 10 |  | 0.73
14 | 19 | 9 | 10 |  | 0.67
15 | 16 | 8 | 8 |  | 0.58
16 | 17 | 7 | 10 |  | 0.61
17 | 21 | 11 | 10 |  | 0.65
18 | 20 | 10 | 10 |  | 0.87
19 | 25 | 15 | 10 |  | 0.77
20 | 19 | 9 | 10 |  | 0.72
21 | 19 | 9 | 10 |  | 0.66
22 | 20 | 10 | 10 |  | 0.72
23 | 21 | 10 | 11 |  | 0.69
24 | 16 | 6 | 10 |  | 0.88
25 | 22 | 11 | 11 |  | 0.8
26 | 19 | 9 | 10 |  | 0.89
27 | 20 | 10 | 10 |  | 0.57
28 | 21 | 10 | 11 |  | 0.62
29 | 16 | 6 | 10 |  | 0.67
30 | 20 | 10 | 10 |  | 0.66
31 | 20 | 10 | 10 |  | 0.71
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Jesse Reigard
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Jesse Reigard |  | 2021-09-10
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541 ) 572-5494 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | SLEEPY HOLLOW |  | ID# 4194283 |  | Month/Year: | 2021-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2 | 28 | 56 | 17.3 | 7 | 26.178 | YES
2 | 2.5 | 28 | 70 | 18 | 7.3 | 29.568 | YES
3 | 2.5 | 28 | 70 | 17.6 | 7.7 | 35.2127 | YES
4 | 1.5 | 28 | 42 | 17.7 | 6.9 | 23.183 | YES
5 | 2 | 28 | 56 | 18.2 | 6.6 | 21.2208 | YES
6 | 2 | 28 | 56 | 18.4 | 6.4 | 19.421 | YES
7 | 3 | 28 | 84 | 18.5 | 6.2 | 20.0853 | YES
8 | 3 | 28 | 84 | 17.9 | 6.8 | 26.1726 | YES
9 | 1.5 | 28 | 42 | 17.8 | 7 | 23.904 | YES
10 | 2 | 28 | 56 | 18.1 | 7.4 | 28.7911 | YES
11 | 2.5 | 28 | 70 | 18.4 | 5.7 | 15.7991 | YES
12 | 2 | 28 | 56 | 18 | 5.3 | 13.1469 | YES
13 | 3 | 28 | 84 | 17.9 | 5.8 | 17.9944 | YES
14 | 1.5 | 28 | 42 | 18.5 | 6.6 | 19.6285 | YES
15 | 2 | 28 | 56 | 18.3 | 6.7 | 21.8828 | YES
16 | 2 | 28 | 56 | 17.8 | 7 | 25.3148 | YES
17 | 1.5 | 28 | 42 | 17.6 | 7.4 | 28.1179 | YES
18 | 2.5 | 28 | 70 | 18.2 | 6.2 | 19.3462 | YES
19 | 3 | 28 | 84 | 18.6 | 6.8 | 24.9721 | YES
20 | 3 | 28 | 84 | 18.3 | 6 | 18.8839 | YES
21 | 2 | 28 | 56 | 17.8 | 6.9 | 24.3883 | YES
22 | 2 | 28 | 56 | 17.7 | 6.8 | 23.6532 | YES
23 | 2.5 | 28 | 70 | 18.1 | 6.4 | 20.9971 | YES
24 | 1.5 | 28 | 42 | 18.5 | 7.7 | 29.5953 | YES
25 | 3 | 28 | 84 | 18.3 | 6.6 | 23.6483 | YES
26 | 1.5 | 28 | 42 | 18 | 7 | 23.5847 | YES
27 | 2 | 28 | 56 | 18.3 | 7.8 | 32.9487 | YES
28 | 2.5 | 28 | 70 | 18.6 | 7.3 | 28.4058 | YES
29 | 3 | 28 | 84 | 18.1 | 6.1 | 19.8753 | YES
30 | 2.5 | 28 | 70 | 17.9 | 6.3 | 20.499 | YES
31 | 2.5 | 28 | 70 | 18.4 | 6.8 | 23.8991 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2