## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | C00S
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-11-01
System Name: | SLEEPY HOLLOW RV PARK |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 25 | 15 | 10 |  | 0.8
2 | 21 | 11 | 10 |  | 0.73
3 | 22 | 11 | 11 |  | 0.76
4 | 25 | 15 | 10 |  | 0.83
5 | 20 | 10 | 10 |  | 0.66
6 | 21 | 11 | 10 |  | 0.68
7 | 19 | 9 | 10 |  | 0.62
8 | 20 | 10 | 10 |  | 0.59
9 | 22 | 11 | 11 |  | 0.65
10 | 20 | 10 | 10 |  | 0.69
11 | 17 | 7 | 10 |  | 0.77
12 | 20 | 10 | 10 |  | 0.73
13 | 18 | 8 | 10 |  | 0.79
14 | 20 | 10 | 10 |  | 0.83
15 | 22 | 11 | 11 |  | 0.85
16 | 20 | 10 | 10 |  | 0.77
17 | 22 | 11 | 11 |  | 0.73
18 | 20 | 10 | 10 |  | 0.63
19 | 21 | 11 | 10 |  | 0.65
20 | 19 | 9 | 10 |  | 0.68
21 | 18 | 8 | 10 |  | 0.73
22 | 21 | 11 | 10 |  | 0.79
23 | 20 | 10 | 10 |  | 0.77
24 | 21 | 11 | 10 |  | 0.68
25 | 18 | 8 | 10 |  | 0.52
26 | 16 | 8 | 8 |  | 0.59
27 | 17 | 7 | 10 |  | 0.64
28 | 20 | 10 | 10 |  | 0.7
29 | 18 | 8 | 10 |  | 0.69
30 | 20 | 10 | 10 |  | 0.76
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Jesse Reigard
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Jesse Reigard |  | 2021-12-10
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541 ) 572-5494 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | SLEEPY HOLLOW |  | ID# 4194283 |  | Month/Year: | 2021-11-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.5 | 28 | 42 | 16.9 | 6.6 | 21.8692 | YES
2 | 2 | 28 | 56 | 16.6 | 6.1 | 19.5978 | YES
3 | 2 | 28 | 56 | 17.2 | 5.5 | 14.9935 | YES
4 | 3 | 28 | 84 | 17.6 | 5.9 | 19.0699 | YES
5 | 3 | 28 | 84 | 16.9 | 7.3 | 33.6825 | YES
6 | 2 | 28 | 56 | 17.5 | 7 | 25.8293 | YES
7 | 2.5 | 28 | 70 | 17.1 | 6.6 | 24.205 | YES
8 | 2 | 28 | 56 | 16.8 | 7.8 | 36.4066 | YES
9 | 2.5 | 28 | 70 | 17.1 | 7.3 | 31.3985 | YES
10 | 3 | 28 | 84 | 17.7 | 6.2 | 21.201 | YES
11 | 3 | 28 | 84 | 17.3 | 5.6 | 17.3802 | YES
12 | 2 | 28 | 56 | 17 | 5.9 | 17.6884 | YES
13 | 2.5 | 28 | 70 | 16.5 | 6.1 | 20.9035 | YES
14 | 2.5 | 28 | 70 | 16.2 | 6.7 | 26.6875 | YES
15 | 2.5 | 28 | 70 | 16.8 | 6.5 | 23.793 | YES
16 | 3 | 28 | 84 | 16.3 | 7.2 | 33.7827 | YES
17 | 3 | 28 | 84 | 16.9 | 7.5 | 36.2654 | YES
18 | 1.5 | 28 | 42 | 17.2 | 7.8 | 33.4933 | YES
19 | 1.5 | 28 | 42 | 16.8 | 6.7 | 22.8565 | YES
20 | 2 | 28 | 56 | 16.5 | 6.3 | 21.2693 | YES
21 | 2 | 28 | 56 | 16.1 | 5.8 | 18.1076 | YES
22 | 2.5 | 28 | 70 | 16.7 | 5.1 | 14.1265 | YES
23 | 2 | 28 | 56 | 17.2 | 6.2 | 19.5387 | YES
24 | 3 | 28 | 84 | 17.5 | 6.8 | 26.8835 | YES
25 | 2.5 | 28 | 70 | 17 | 7.3 | 31.6086 | YES
26 | 2.5 | 28 | 70 | 16.7 | 6.9 | 27.8014 | YES
27 | 3 | 28 | 84 | 16.5 | 6.4 | 24.7692 | YES
28 | 2.5 | 28 | 70 | 16.3 | 6.9 | 28.5552 | YES
29 | 2 | 28 | 56 | 16 | 7 | 28.5582 | YES
30 | 2 | 28 | 56 | 16.3 | 5.8 | 17.8632 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2