## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | C00S
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-01-22
System Name: | SLEEPY HOLLOW RV PARK |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 | 8 | 10 |  | 0.89
2 | 20 | 10 | 10 |  | 0.76
3 | 16 | 8 | 8 |  | 0.83
4 | 23 | 13 | 10 |  | 0.67
5 | 20 | 10 | 10 |  | 0.85
6 | 21 | 11 | 10 |  | 0.79
7 | 25 | 15 | 10 |  | 0.59
8 | 20 | 10 | 10 |  | 0.78
9 | 22 | 12 | 10 |  | 0.84
10 | 20 | 10 | 10 |  | 0.64
11 | 16 | 6 | 10 |  | 0.78
12 | 19 | 9 | 10 |  | 0.9
13 | 20 | 10 | 10 |  | 0.97
14 | 20 | 10 | 10 |  | 0.92
15 | 19 | 9 | 10 |  | 0.87
16 | 17 | 6 | 11 |  | 0.83
17 | 18 | 9 | 9 |  | 0.85
18 | 20 | 10 | 10 |  | 0.68
19 | 21 | 11 | 10 |  | 0.88
20 | 20 | 10 | 10 |  | 0.79
21 | 19 | 9 | 10 |  | 0.74
22 | 21 | 11 | 10 |  | 0.89
23 | 18 | 8 | 10 |  | 0.76
24 | 16 | 6 | 10 |  | 0.59
25 | 19 | 9 | 10 |  | 0.77
26 | 20 | 10 | 10 |  | 0.81
27 | 21 | 11 | 10 |  | 0.84
28 | 19 | 9 | 10 |  | 0.76
29 | 18 | 8 | 10 |  | 0.78
30 | 20 | 10 | 10 |  | 0.69
31 | 17 | 7 | 10 |  | 0.81
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Jesse Reigard
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Jesse Reigard |  | 2022-02-04
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541 ) 572-5494 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | SLEEPY HOLLOW |  | ID# 4194283 |  | Month/Year: | 2022-01-22 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.5 | 28 | 42 | 15.9 | 7.1 | 28.1817 | YES
2 | 2 | 28 | 56 | 15.6 | 6.7 | 26.2374 | YES
3 | 2 | 28 | 56 | 15.9 | 5.8 | 18.3552 | YES
4 | 1.5 | 28 | 42 | 16.5 | 5.6 | 15.4115 | YES
5 | 3 | 28 | 84 | 16.9 | 6.2 | 22.3761 | YES
6 | 3 | 28 | 84 | 16.3 | 4.8 | 13.7313 | YES
7 | 1.5 | 28 | 42 | 15.8 | 5.2 | 13.8834 | YES
8 | 2.5 | 28 | 70 | 15.4 | 5.1 | 15.444 | YES
9 | 2.5 | 28 | 70 | 14.8 | 6.2 | 24.3329 | YES
10 | 3 | 28 | 84 | 15.1 | 6.8 | 31.5599 | YES
11 | 1.5 | 28 | 42 | 15.4 | 7.4 | 32.566 | YES
12 | 1.5 | 28 | 42 | 15.8 | 7.9 | 38.1433 | YES
13 | 3 | 28 | 84 | 16.3 | 6.7 | 28.0688 | YES
14 | 3 | 28 | 84 | 16.5 | 6.3 | 23.862 | YES
15 | 2.5 | 28 | 70 | 15.7 | 5.9 | 20.4692 | YES
16 | 2 | 28 | 56 | 15.3 | 6.3 | 23.0609 | YES
17 | 2 | 28 | 56 | 15.1 | 6.6 | 26.1402 | YES
18 | 2.5 | 28 | 70 | 14.6 | 6.2 | 24.662 | YES
19 | 3 | 28 | 84 | 14.4 | 6 | 24.5679 | YES
20 | 1.5 | 28 | 42 | 14.9 | 5.7 | 17.852 | YES
21 | 1.5 | 28 | 42 | 15.2 | 5.9 | 18.8622 | YES
22 | 2 | 28 | 56 | 15.7 | 7 | 29.1366 | YES
23 | 2 | 28 | 56 | 15.3 | 6.3 | 23.0609 | YES
24 | 1.5 | 28 | 42 | 15.8 | 6.6 | 23.5506 | YES
25 | 2.5 | 28 | 70 | 16.1 | 7.4 | 34.8257 | YES
26 | 1.5 | 28 | 42 | 16.4 | 5.7 | 16.1178 | YES
27 | 2 | 28 | 56 | 16.7 | 6.2 | 20.2111 | YES
28 | 2 | 28 | 56 | 16 | 5.9 | 18.9312 | YES
29 | 2.5 | 28 | 70 | 15.3 | 6.3 | 24.4236 | YES
30 | 3 | 28 | 84 | 15.6 | 6.7 | 29.4134 | YES
31 | 3 | 28 | 84 | 15.1 | 7.4 | 39.39 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2