## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-07-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 13 | 0 | 13 | OK | 0.13
2 | 13 | 0 | 13 | OK | 0.1
3 | 13 | 0 | 13 | OK | 0.16
4 | 14 | 1 | 13 | OK | 0.13
5 | 5 | 1 | 4 | OK | 0.33
6 | 4 | 1 | 3 | OK | 0.15
7 | 4 | 1 | 3 | OK | 0.14
8 | 3 | 1 | 2 | OK | 0.31
9 | 4 | 1 | 3 | OK | 0.12
10 | 4 | 1 | 3 | OK | 0.15
11 | 5 | 1 | 4 | OK | 0.1
12 | 5 | 1 | 4 | OK | 0.16
13 | 5 | 1 | 4 | OK | 0.13
14 | 6 | 1 | 5 | OK | 0.61
15 | 6 | 1 | 5 | OK | 0.34
16 | 6 | 1 | 5 | OK | 0.19
17 | 6 | 1 | 5 | OK | 0.18
18 | 6 | 1 | 5 | OK | 0.12
19 | 6 | 1 | 5 | OK | 0.12
20 | 4 | 1 | 3 | OK | 0.09
21 | 4 | 1 | 3 | OK | 0.08
22 | 4 | 1 | 3 | OK | 0.13
23 | 4 | 1 | 3 | OK | 0.23
24 | 4 | 1 | 3 | OK | 0.06
25 | 9 | 1 | 8 | OK | 0.1
26 | 9 | 1 | 8 | OK | 0.13
27 | 6 | 1 | 5 | OK | 0.08
28 | 4 | 1 | 3 | OK | 0.09
29 | 5 | 1 | 4 | OK | 0.33
30 | 5 | 1 | 4 | OK | 0.24
31 | 6 | 1 | 5 | OK | 0.18
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-08-07
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-07-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.88 | 60 | 52.8 | 15 | 7.11 | 13.9939 | YES | 25
2 | 0.92 | 60 | 55.2 | 16 | 7.1 | 13.0987 | YES | 25
3 | 0.76 | 60 | 45.6 | 16.1 | 7.25 | 13.5085 | YES | 25
4 | 1.02 | 60 | 61.2 | 17.3 | 7.34 | 13.2787 | YES | 25
5 | 0.73 | 60 | 43.8 | 17.2 | 7.35 | 12.9798 | YES | 25
6 | 0.62 | 60 | 37.2 | 17.4 | 7.46 | 13.1754 | YES | 25
7 | 0.58 | 60 | 34.8 | 17.5 | 7.39 | 12.6923 | YES | 25
8 | 0.72 | 60 | 43.2 | 16.9 | 7.4 | 13.4767 | YES | 25
9 | 0.35 | 60 | 21 | 16.7 | 7.42 | 13.1902 | YES | 25
10 | 0.35 | 60 | 21 | 16.6 | 7.27 | 12.5574 | YES | 25
11 | 0.5 | 60 | 30 | 16.4 | 7.2 | 12.6143 | YES | 25
12 | 0.65 | 60 | 39 | 16.3 | 7.17 | 12.7758 | YES | 25
13 | 0.75 | 60 | 45 | 15.8 | 7.34 | 14.2349 | YES | 25
14 | 1.14 | 60 | 68.4 | 16.7 | 7.58 | 15.3191 | YES | 25
15 | 0.77 | 60 | 46.2 | 16.2 | 7.54 | 14.9614 | YES | 25
16 | 0.67 | 60 | 40.2 | 16.3 | 7.48 | 14.3697 | YES | 25
17 | 0.56 | 60 | 33.6 | 15.6 | 7.2 | 13.4011 | YES | 25
18 | 0.67 | 60 | 40.2 | 16.1 | 7.2 | 13.1237 | YES | 25
19 | 0.75 | 60 | 45 | 15.9 | 7.2 | 13.4231 | YES | 25
20 | 0.78 | 60 | 46.8 | 16.9 | 7.25 | 12.8327 | YES | 25
21 | 0.75 | 60 | 45 | 16.8 | 7.24 | 12.8269 | YES | 25
22 | 0.72 | 60 | 43.2 | 16.6 | 7.3 | 13.2481 | YES | 25
23 | 0.76 | 60 | 45.6 | 16.5 | 7.18 | 12.813 | YES | 25
24 | 0.69 | 60 | 41.4 | 16.5 | 7.06 | 12.1545 | YES | 25
25 | 0.72 | 60 | 43.2 | 16.7 | 7.21 | 12.7259 | YES | 25
26 | 0.68 | 60 | 40.8 | 16.4 | 7.24 | 13.0704 | YES | 25
27 | 0.63 | 60 | 37.8 | 16.4 | 7.2 | 12.8036 | YES | 25
28 | 0.72 | 60 | 43.2 | 16.5 | 7.17 | 12.707 | YES | 25
29 | 0.83 | 60 | 49.8 | 16 | 7.1 | 12.9645 | YES | 25
30 | 0.55 | 60 | 33 | 17.2 | 7.1 | 11.5825 | YES | 25
31 | 0.79 | 60 | 47.4 | 16.5 | 7.15 | 12.7142 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2