## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-08-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 6 | 1 | 5 | OK | 0.11
2 | 6 | 1 | 5 | OK | 0.25
3 | 7 | 1 | 6 | OK | 0.15
4 | 4 | 1 | 3 | OK | 0.11
5 | 4 | 1 | 3 | OK | 0.22
6 | 4 | 1 | 3 | OK | 0.17
7 | 5 | 1 | 4 | OK | 0.12
8 | 5 | 1 | 4 | OK | 0.34
9 | 9 | 1 | 8 | OK | 0.43
10 | 4 | 1 | 3 | OK | 0.1
11 | 19 | 1 | 18 | OK | 0.11
12 | 4 | 1 | 3 | OK | 0.09
13 | 4 | 1 | 3 | OK | 0.15
14 | 4 | 1 | 3 | OK | 0.11
15 | 1 | 1 | 0 | OK | 0.09
16 | 4 | 1 | 3 | OK | 0.19
17 | 4 | 1 | 3 | OK | 0.14
18 | 4 | 1 | 3 | OK | 0.11
19 | 5 | 1 | 4 | OK | 0.3
20 | 5 | 1 | 4 | OK | 0.18
21 | 5 | 2 | 3 | OK | 0.24
22 | 5 | 1 | 4 | OK | 0.21
23 | 5 | 1 | 4 | OK | 0.12
24 | 6 | 1 | 5 | OK | 0.08
25 | 7 | 1 | 6 | OK | 0.11
26 | 8 | 1 | 7 | OK | 0.15
27 | 8 | 1 | 7 | OK | 0.1
28 | 7 | 1 | 6 | OK | 0.14
29 | 4 | 1 | 3 | OK | 0.11
30 | 4 | 1 | 3 | OK | 0.08
31 | 4 | 1 | 3 | OK | 0.07
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-09-05
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-08-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.79 | 60 | 47.4 | 16.8 | 7.14 | 12.4144 | YES | 25
2 | 0.46 | 60 | 27.6 | 17.1 | 7.2 | 11.98 | YES | 25
3 | 0.62 | 60 | 37.2 | 17.1 | 7.43 | 13.2937 | YES | 25
4 | 0.58 | 60 | 34.8 | 16.9 | 7.38 | 13.1643 | YES | 25
5 | 0.53 | 60 | 31.8 | 17.1 | 7.2 | 12.0766 | YES | 25
6 | 0.66 | 60 | 39.6 | 16.5 | 7.24 | 12.9534 | YES | 25
7 | 0.66 | 60 | 39.6 | 16.3 | 7.1 | 12.4611 | YES | 25
8 | 0.83 | 60 | 49.8 | 17 | 7.26 | 12.868 | YES | 25
9 | 0.74 | 60 | 44.4 | 16.8 | 7 | 11.715 | YES | 25
10 | 0.78 | 60 | 46.8 | 16.7 | 7.54 | 14.4864 | YES | 25
11 | 0.81 | 60 | 48.6 | 16.9 | 7.46 | 13.9232 | YES | 25
12 | 0.34 | 60 | 20.4 | 16.4 | 7.15 | 12.1563 | YES | 25
13 | 0.72 | 60 | 43.2 | 16.2 | 7.32 | 13.7094 | YES | 25
14 | 0.68 | 60 | 40.8 | 16.2 | 7.26 | 13.3457 | YES | 25
15 | 0.55 | 60 | 33 | 16.7 | 7.15 | 12.2042 | YES | 25
16 | 0.56 | 60 | 33.6 | 17.8 | 7.23 | 11.6914 | YES | 25
17 | 0.43 | 60 | 25.8 | 17 | 7.16 | 11.8411 | YES | 25
18 | 0.39 | 60 | 23.4 | 16.9 | 7.38 | 12.881 | YES | 25
19 | 0.41 | 60 | 24.6 | 16.5 | 7.32 | 12.9685 | YES | 25
20 | 0.37 | 60 | 22.2 | 16.2 | 7.16 | 12.4093 | YES | 25
21 | 0.23 | 60 | 13.8 | 16.4 | 7.33 | 12.8371 | YES | 25
22 | 0.35 | 60 | 21 | 16.8 | 7.04 | 11.3703 | YES | 25
23 | 0.53 | 60 | 31.8 | 16.5 | 7.25 | 12.8096 | YES | 25
24 | 0.4 | 60 | 24 | 16.8 | 7.23 | 12.2767 | YES | 25
25 | 0.55 | 60 | 33 | 16.1 | 7.11 | 12.5178 | YES | 25
26 | 0.54 | 60 | 32.4 | 16.4 | 7.1 | 12.2085 | YES | 25
27 | 0.5 | 60 | 30 | 16.5 | 7.05 | 11.848 | YES | 25
28 | 0.51 | 60 | 30.6 | 16.6 | 7.07 | 11.8705 | YES | 25
29 | 0.61 | 60 | 36.6 | 16.5 | 6.95 | 11.5587 | YES | 25
30 | 0.78 | 60 | 46.8 | 16.2 | 6.98 | 12.1622 | YES | 25
31 | 0.6 | 60 | 36 | 15.8 | 7.03 | 12.4684 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2