## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-09-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 4 | 1 | 3 | OK | 0.08
2 | 4 | 1 | 3 | OK | 0.07
3 | 6 | 1 | 5 | OK | 0.07
4 | 6 | 1 | 5 | OK | 0.17
5 | 6 | 1 | 5 | OK | 0.12
6 | 6 | 1 | 5 | OK | 0.1
7 | 7 | 1 | 6 | OK | 0.07
8 | 7 | 1 | 6 | OK | 0.06
9 | 7 | 1 | 6 | OK | 0.07
10 | 8 | 1 | 7 | OK | 0.19
11 | 8 | 1 | 7 | OK | 0.1
12 | 5 | 1 | 4 | OK | 0.18
13 | 5 | 1 | 4 | OK | 0.1
14 | 5 | 1 | 4 | OK | 0.07
15 | 6 | 1 | 5 | OK | 0.06
16 | 6 | 1 | 5 | OK | 0.07
17 | 7 | 1 | 6 | OK | 0.15
18 | 8 | 1 | 7 | OK | 0.1
19 | 8 | 1 | 7 | OK | 0.13
20 | 8 | 1 | 7 | OK | 0.11
21 | 9 | 1 | 8 | OK | 0.11
22 | 9 | 1 | 8 | OK | 0.08
23 | 9 | 1 | 8 | OK | 0.22
24 | 10 | 1 | 9 | OK | 0.13
25 | 10 | 1 | 9 | OK | 0.06
26 | 10 | 1 | 9 | OK | 0.07
27 | 10 | 1 | 9 | OK | 0.06
28 | 10 | 1 | 9 | OK | 0.12
29 | 10 | 1 | 9 | OK | 0.08
30 | 10 | 1 | 9 | OK | 0.21
31 |  |  |  | Change Filter
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-10-06
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 60 | 36 | 15.5 | 7.01 | 12.6275 | YES | 25
2 | 0.6 | 60 | 36 | 15.8 | 7.03 | 12.4684 | YES
3 | 0.55 | 60 | 33 | 15.3 | 7.03 | 12.8202 | YES
4 | 0.87 | 60 | 52.2 | 16 | 7 | 12.5477 | YES
5 | 0.75 | 60 | 45 | 16.4 | 6.97 | 11.914 | YES
6 | 0.67 | 60 | 40.2 | 16.1 | 6.91 | 11.7787 | YES
7 | 0.74 | 60 | 44.4 | 16.5 | 6.94 | 11.6889 | YES
8 | 0.83 | 60 | 49.8 | 16.4 | 6.95 | 11.9345 | YES
9 | 0.76 | 60 | 45.6 | 15.8 | 6.98 | 12.4647 | YES
10 | 0.78 | 60 | 46.8 | 16.1 | 7 | 12.3358 | YES
11 | 0.73 | 60 | 43.8 | 16 | 7.02 | 12.4404 | YES
12 | 0.58 | 60 | 34.8 | 15.9 | 7 | 12.2191 | YES
13 | 0.72 | 60 | 43.2 | 15.8 | 7 | 12.5005 | YES
14 | 0.8 | 60 | 48 | 15.7 | 6.93 | 12.3735 | YES
15 | 0.77 | 60 | 46.2 | 15.5 | 6.89 | 12.3127 | YES
16 | 0.76 | 60 | 45.6 | 15.6 | 6.9 | 12.2619 | YES
17 | 0.75 | 60 | 45 | 15.2 | 6.87 | 12.4413 | YES
18 | 0.64 | 60 | 38.4 | 15.8 | 6.97 | 12.2486 | YES
19 | 0.7 | 60 | 42 | 15.5 | 6.96 | 12.5372 | YES
20 | 0.54 | 60 | 32.4 | 15.5 | 6.95 | 12.2635 | YES
21 | 0.6 | 60 | 36 | 15.3 | 7.04 | 12.9419 | YES
22 | 0.48 | 60 | 28.8 | 15.8 | 6.97 | 12.0258 | YES
23 | 0.36 | 60 | 21.6 | 16.1 | 7.1 | 12.2025 | YES
24 | 0.32 | 60 | 19.2 | 16.3 | 6.98 | 11.4591 | YES
25 | 0.59 | 60 | 35.4 | 15.7 | 6.93 | 12.079 | YES
26 | 0.6 | 60 | 36 | 14.9 | 6.93 | 12.7601 | YES
27 | 0.62 | 60 | 37.2 | 15.6 | 6.91 | 12.1116 | YES
28 | 0.65 | 60 | 39 | 15.2 | 6.91 | 12.4843 | YES
29 | 0.65 | 60 | 39 | 14.5 | 6.95 | 13.2807 | YES
30 | 0.56 | 60 | 33.6 | 14.9 | 6.96 | 12.8445 | YES
31 |  | 60
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2