## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-10-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 29 | 1 | 28 | Change Filter | 0.08 | 0.08
2 | 29 | 1 | 28 | Change Filter | 0.16 | 0.16
3 | 30 | 1 | 29 | Change Filter | 0.11 | 0.11
4 | 30 | 1 | 29 | Change Filter | 0.17 | 0.17
5 | 30 | 1 | 29 | Change Filter | 0.06 | 0.06
6 | 31 | 1 | 30 | Change Filter | 0.06 | 0.06
7 | 31 | 1 | 30 | Change Filter | 0.11 | 0.11
8 | 31 | 1 | 30 | Change Filter | 0.06 | 0.06
9 | 32 | 1 | 31 | Change Filter | 0.06 | 0.06
10 | 32 | 1 | 31 | Change Filter | 0.14 | 0.14
11 | 33 | 1 | 32 | Change Filter | 0.11 | 0.11
12 | 35 | 1 | 34 | Change Filter | 0.06 | 0.06
13 | 30 | 1 | 29 | Change Filter | 0.07 | 0.07
14 | 30 | 1 | 29 | Change Filter | 0.18 | 0.18
15 | 30 | 1 | 29 | Change Filter | 0.28 | 0.28
16 | 29 | 1 | 28 | Change Filter | 0.23 | 0.23
17 | 29 | 1 | 28 | Change Filter | 0.14 | 0.14
18 | 29 | 1 | 28 | Change Filter | 0.22 | 0.22
19 | 28 | 1 | 27 | OK | 0.07 | 0.07
20 | 28 | 1 | 27 | OK | 0.12 | 0.12
21 | 30 | 1 | 29 | Change Filter | 0.08 | 0.08
22 | 29 | 1 | 28 | Change Filter | 0.15 | 0.15
23 | 28 | 1 | 27 | OK | 0.09 | 0.09
24 | 29 | 1 | 28 | Change Filter | 0.15 | 0.15
25 | 30 | 1 | 29 | Change Filter | 0.17 | 0.17
26 | 31 | 1 | 30 | Change Filter | 0.09 | 0.09
27 | 30 | 1 | 29 | Change Filter | 0.07 | 0.07
28 | 30 | 1 | 29 | Change Filter | 0.08 | 0.08
29 | 27 | 1 | 26 | OK | 0.08 | 0.08
30 | 27 | 1 | 26 | OK | 0.11 | 0.11
31 | 27 | 1 | 26 | OK | 0.09 | 0.09
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-11-05
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-10-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.54 | 60 | 32.4 | 15.7 | 7 | 12.3277 | YES | 25
2 | 0.64 | 60 | 38.4 | 15.1 | 7.08 | 13.3743 | YES | 25
3 | 0.54 | 60 | 32.4 | 15.5 | 7 | 12.4943 | YES | 25
4 | 0.46 | 60 | 27.6 | 14.9 | 6.99 | 12.8409 | YES | 25
5 | 0.57 | 60 | 34.2 | 16 | 6.96 | 11.9437 | YES | 25
6 | 0.6 | 60 | 36 | 14.5 | 6.87 | 12.8174 | YES | 25
7 | 0.68 | 60 | 40.8 | 15.2 | 6.96 | 12.7629 | YES | 25
8 | 0.62 | 60 | 37.2 | 14.4 | 6.87 | 12.9332 | YES | 25
9 | 0.64 | 60 | 38.4 | 15 | 6.85 | 12.3589 | YES | 25
10 | 0.66 | 60 | 39.6 | 14.6 | 6.91 | 13.0119 | YES | 25
11 | 0.58 | 60 | 34.8 | 14.4 | 7 | 13.5123 | YES | 25
12 | 0.63 | 60 | 37.8 | 15.8 | 6.94 | 12.0984 | YES | 25
13 | 0.65 | 60 | 39 | 15.5 | 6.92 | 12.281 | YES | 25
14 | 0.64 | 60 | 38.4 | 14.8 | 6.9 | 12.7615 | YES | 25
15 | 0.7 | 60 | 42 | 14.4 | 7.03 | 13.8526 | YES | 25
16 | 0.58 | 60 | 34.8 | 14.8 | 7.08 | 13.5524 | YES | 25
17 | 0.51 | 60 | 30.6 | 14.2 | 7.11 | 14.1521 | YES | 25
18 | 0.62 | 60 | 37.2 | 13.6 | 7.14 | 15.0841 | YES | 25
19 | 0.61 | 60 | 36.6 | 14.5 | 6.99 | 13.4182 | YES | 25
20 | 0.75 | 60 | 45 | 14.2 | 6.92 | 13.554 | YES | 25
21 | 0.67 | 60 | 40.2 | 14.3 | 6.95 | 13.4906 | YES | 25
22 | 0.61 | 60 | 36.6 | 14 | 7.05 | 14.1877 | YES | 25
23 | 0.72 | 60 | 43.2 | 13.2 | 6.92 | 14.4421 | YES | 25
24 | 0.59 | 60 | 35.4 | 13.3 | 6.92 | 14.1345 | YES | 25
25 | 0.59 | 60 | 35.4 | 13.7 | 7.11 | 14.7673 | YES | 25
26 | 0.73 | 60 | 43.8 | 14 | 6.92 | 13.7053 | YES | 25
27 | 0.71 | 60 | 42.6 | 14.1 | 6.87 | 13.3325 | YES | 25
28 | 0.7 | 60 | 42 | 13.6 | 6.82 | 13.517 | YES | 25
29 | 1.22 | 60 | 73.2 | 12.9 | 6.85 | 15.1993 | YES | 25
30 | 0.54 | 60 | 32.4 | 13.4 | 7 | 14.3814 | YES | 25
31 | 0.34 | 60 | 20.4 | 13.5 | 6.95 | 13.7059 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2