## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-11-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 16 | 1 | 15 | OK | 0.12
2 | 16 | 1 | 15 | OK | 0.08
3 | 16 | 1 | 15 | OK | 0.09
4 | 17 | 1 | 16 | OK | 0.12
5 | 17 | 1 | 16 | OK | 0.15
6 | 17 | 1 | 16 | OK | 0.33
7 | 17 | 1 | 16 | OK | 0.17
8 | 17 | 1 | 16 | OK | 0.15
9 | 17 | 1 | 16 | OK | 0.14
10 | 17 | 1 | 16 | OK | 0.09
11 | 17 | 1 | 16 | OK | 0.2
12 | 17 | 1 | 16 | OK | 0.22
13 | 17 | 1 | 16 | OK | 0.16
14 | 18 | 1 | 17 | OK | 0.19
15 | 18 | 1 | 17 | OK | 0.12
16 | 18 | 1 | 17 | OK | 0.15
17 | 18 | 1 | 17 | OK | 0.13
18 | 18 | 1 | 17 | OK | 0.16
19 | 18 | 1 | 17 | OK | 0.27
20 | 18 | 1 | 17 | OK | 0.18
21 | 18 | 1 | 17 | OK | 0.19
22 | 18 | 1 | 17 | OK | 0.28
23 | 18 | 1 | 17 | OK | 0.17
24 | 18 | 1 | 17 | OK | 0.2
25 | 18 | 1 | 17 | OK | 0.28
26 | 18 | 1 | 17 | OK | 0.24
27 | 18 | 1 | 17 | OK | 0.2
28 | 18 | 1 | 17 | OK | 0.17
29 | 18 | 1 | 17 | OK | 0.16
30 | 18 | 1 | 17 | OK | 0.22
31 |  |  |  | Change Filter
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-12-03
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-11-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.38 | 60 | 22.8 | 13.3 | 6.93 | 13.8508 | YES | 25
2 | 0.7 | 60 | 42 | 13 | 6.91 | 14.549 | YES | 25
3 | 0.41 | 60 | 24.6 | 12.5 | 6.81 | 14.0231 | YES | 25
4 | 0.41 | 60 | 24.6 | 12.6 | 6.75 | 13.6224 | YES | 25
5 | 0.38 | 60 | 22.8 | 12.2 | 6.76 | 14.4499 | YES | 25
6 | 0.67 | 60 | 40.2 | 12.4 | 6.82 | 15.0174 | YES | 25
7 | 0.64 | 60 | 38.4 | 12.7 | 6.8 | 14.1524 | YES | 25
8 | 0.56 | 60 | 33.6 | 12.7 | 6.87 | 14.393 | YES | 25
9 | 0.65 | 60 | 39 | 12.9 | 6.8 | 13.9803 | YES | 25
10 | 0.63 | 60 | 37.8 | 13 | 6.82 | 13.9588 | YES | 25
11 | 0.67 | 60 | 40.2 | 12.5 | 7 | 15.5003 | YES | 25
12 | 0.68 | 60 | 40.8 | 12.6 | 6.92 | 14.9643 | YES | 25
13 | 0.66 | 60 | 39.6 | 12.7 | 6.91 | 14.7759 | YES | 25
14 | 0.54 | 60 | 32.4 | 12.5 | 6.92 | 14.826 | YES | 25
15 | 0.5 | 60 | 30 | 11.9 | 6.64 | 14.3299 | YES | 25
16 | 0.41 | 60 | 24.6 | 12 | 6.69 | 14.3409 | YES | 25
17 | 0.46 | 60 | 27.6 | 12.1 | 6.6 | 13.908 | YES | 25
18 | 0.32 | 60 | 19.2 | 11.3 | 6.7 | 14.8874 | YES | 25
19 | 0.88 | 60 | 52.8 | 11.4 | 6.72 | 15.8197 | YES | 25
20 | 0.87 | 60 | 52.2 | 12 | 6.7 | 15.1147 | YES | 25
21 | 0.97 | 60 | 58.2 | 11.8 | 6.74 | 15.6811 | YES | 25
22 | 0.79 | 60 | 47.4 | 12.3 | 6.7 | 14.7067 | YES | 25
23 | 0.69 | 60 | 41.4 | 11.7 | 6.67 | 14.9562 | YES | 25
24 | 0.69 | 60 | 41.4 | 11.3 | 6.65 | 15.2342 | YES | 25
25 | 0.8 | 60 | 48 | 12 | 6.74 | 15.2035 | YES | 25
26 | 0.62 | 60 | 37.2 | 11 | 6.63 | 15.3048 | YES | 25
27 | 0.72 | 60 | 43.2 | 10 | 6.82 | 17.5835 | YES | 25
28 | 0.61 | 60 | 36.6 | 8.8 | 6.74 | 18.2587 | YES | 25
29 | 0.71 | 60 | 42.6 | 9.2 | 6.76 | 18.1153 | YES | 25
30 | 0.69 | 60 | 41.4 | 9.3 | 6.76 | 17.9593 | YES | 25
31 |  | 60 | [5 empty] | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2