## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-02-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 15 | 1 | 14 | OK |  | 0.29
2 | 15 | 1 | 14 | OK |  | 0.25
3 | 6 | 1 | 5 | OK |  | 0.64
4 | 10 | 1 | 9 | OK |  | 0.72
5 | 7 | 1 | 6 | OK |  | 0.36
6 | 7 | 1 | 6 | OK |  | 0.25
7 | 7 | 1 | 6 | OK |  | 0.25
8 | 7 | 1 | 6 | OK |  | 0.35
9 | 7 | 1 | 6 | OK |  | 2.35
10 | 7 | 1 | 6 | OK |  | 0.14
11 | 7 | 1 | 6 | OK |  | 1.86
12 | 7 | 1 | 6 | OK |  | 0.15
13 | 7 | 1 | 6 | OK |  | 1.09
14 | 7 | 1 | 6 | OK |  | 0.49
15 | 7 | 1 | 6 | OK |  | 0.48
16 | 7 | 1 | 6 | OK |  | 0.67
17 | 5 | 1 | 4 | OK |  | 0.42
18 | 5 | 1 | 4 | OK |  | 0.32
19 | 5 | 1 | 4 | OK |  | 0.36
20 | 7 | 1 | 6 | OK |  | 0.36
21 | 7 | 1 | 6 | OK |  | 0.49
22 | 7 | 1 | 6 | OK |  | 0.45
23 | 7 | 1 | 6 | OK |  | 0.4
24 | 20 | 1 | 19 | OK |  | 0.8
25 | 16 | 1 | 15 | OK |  | 0.59
26 | 16 | 1 | 15 | OK |  | 0.57
27 | 3 | 1 | 2 | OK |  | 0.7
28 | 3 | 1 | 2 | OK |  | 0.58
29
30
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: During Feb there were 3 instances of turbidity above 1.0. During this time a new hire was working at the plants. We believe that he may have switched the results on 2 of the occasions. |  |  |  |  | PRINTED NAME: Brenda Vasquez
On the 11th the Raw water Turbidity result was 0.42 & the Treated was 1.86, on the 13th the Raw result was 0.41 and the Treated was 1.09. We are not sure what happened on the 9th. |  |  |  |  | SIGNATURE: Brenda L Vasquez |  | 2025-03-05
It was decided that as of March the employee decided to take on another position at the site. (BV) |  |  |  |  | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-02-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.01 | 60 | 60.6 | 10.4 | 6.91 | 18.2478 | YES | 25
2 | 1.13 | 60 | 67.8 | 9.5 | 6.93 | 19.74 | YES | 25
3 | 0.95 | 60 | 57 | 9.1 | 6.9 | 19.6526 | YES | 25
4 | 1.25 | 60 | 75 | 8.7 | 7.02 | 21.7576 | YES | 25
5 | 1.24 | 60 | 74.4 | 8.7 | 7.07 | 22.1183 | YES | 25
6 | 0.96 | 60 | 57.6 | 7.5 | 6.72 | 20.5153 | YES | 25
7 | 1.12 | 60 | 67.2 | 7.8 | 6.7 | 20.3381 | YES | 25
8 | 1.42 | 60 | 85.2 | 8.7 | 6.81 | 20.6058 | YES | 25
9 | 1.39 | 60 | 83.4 | 8.2 | 6.76 | 20.8534 | YES | 25
10 | 1.44 | 60 | 86.4 | 8.1 | 6.8 | 21.4067 | YES | 25
11 | 1.29 | 60 | 77.4 | 8.5 | 6.81 | 20.5754 | YES | 25
12 | 1.11 | 60 | 66.6 | 5.2 | 6.8 | 24.9911 | YES | 25
13 | 1.29 | 60 | 77.4 | 10.2 | 6.92 | 19.1341 | YES | 25
14 | 1.41 | 60 | 84.6 | 9 | 6.87 | 20.6093 | YES | 25
15 | 1.59 | 60 | 95.4 | 10.7 | 7.1 | 20.3864 | YES | 25
16 | 1.41 | 60 | 84.6 | 10 | 7.01 | 20.2697 | YES | 25
17 | 1.17 | 60 | 70.2 | 10.5 | 6.91 | 18.454 | YES | 25
18 | 1.16 | 60 | 69.6 | 10 | 7.21 | 21.1346 | YES | 25
19 | 1.08 | 60 | 64.8 | 10.4 | 7.11 | 19.706 | YES | 25
20 | 1.23 | 60 | 73.8 | 9.8 | 7.2 | 21.5082 | YES | 25
21 | 1.14 | 60 | 68.4 | 10.3 | 7.27 | 21.1144 | YES | 25
22 | 1.29 | 60 | 77.4 | 10.5 | 7.24 | 20.9721 | YES | 25
23 | 1.12 | 60 | 67.2 | 12.3 | 6.84 | 15.971 | YES | 25
24 | 1.18 | 60 | 70.8 | 11.8 | 6.72 | 15.9339 | YES | 25
25 | 0.84 | 60 | 50.4 | 12.2 | 7.05 | 16.7394 | YES | 25
26 | 0.84 | 60 | 50.4 | 9.5 | 6.93 | 19.1126 | YES | 25
27 | 0.86 | 60 | 51.6 | 11.3 | 6.9 | 16.8841 | YES | 25
28 | 0.88 | 60 | 52.8 | 9.8 | 6.83 | 18.1904 | YES | 25
29
30
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2