## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-03-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 6 | 1 | 5 | OK |  | 0.5
2 | 6 | 1 | 5 | OK |  | 0.39
3 | 6 | 1 | 5 | OK |  | 0.29
4 | 6 | 1 | 5 | OK |  | 0.46
5 | 6 | 1 | 5 | OK |  | 0.35
6 | 6 | 1 | 5 | OK |  | 0.45
7 | 6 | 1 | 5 | OK |  | 0.38
8 | 7 | 1 | 6 | OK |  | 0.42
9 | 7 | 1 | 6 | OK |  | 0.34
10 | 7 | 1 | 6 | OK |  | 0.24
11 | 7 | 1 | 6 | OK |  | 0.19
12 | 8 | 1 | 7 | OK |  | 0.24
13 | 8 | 1 | 7 | OK |  | 0.32
14 | 8 | 1 | 7 | OK |  | 0.95
15 | 8 | 1 | 7 | OK |  | 0.64
16 | 8 | 1 | 7 | OK |  | 0.87
17 | 8 | 1 | 7 | OK |  | 0.9
18 | 8 | 1 | 7 | OK |  | 0.88
19 | 8 | 1 | 7 | OK |  | 0.79
20 | 8 | 1 | 7 | OK |  | 0.63
21 | 8 | 1 | 7 | OK |  | 0.61
22 | 8 | 1 | 7 | OK |  | 0.6
23 | 8 | 1 | 7 | OK |  | 0.62
24 | 8 | 1 | 7 | OK |  | 0.85
25 | 8 | 1 | 7 | OK |  | 0.48
26 | 8 | 1 | 7 | OK |  | 0.62
27 | 8 | 1 | 7 | OK |  | 0.4
28 | 8 | 1 | 7 | OK |  | 0.45
29 | 8 | 1 | 7 | OK |  | 0.5
30 | 8 | 1 | 7 | OK |  | 0.6
31 | 9 | 1 | 8 | OK |  | 0.59
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2025-04-02
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-03-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.86 | 60 | 51.6 | 11.5 | 6.85 | 16.3899 | YES | 25
2 | 0.8 | 60 | 48 | 10.9 | 6.72 | 16.1877 | YES | 25
3 | 0.9 | 60 | 54 | 10.3 | 6.6 | 16.3237 | YES | 25
4 | 0.86 | 60 | 51.6 | 11.4 | 6.6 | 15.1622 | YES | 25
5 | 0.97 | 60 | 58.2 | 9.6 | 6.68 | 17.6764 | YES | 25
6 | 0.84 | 60 | 50.4 | 10.4 | 6.6 | 16.115 | YES | 25
7 | 0.72 | 60 | 43.2 | 10 | 6.73 | 17.0515 | YES | 25
8 | 0.88 | 60 | 52.8 | 10.1 | 6.71 | 17.1251 | YES | 25
9 | 0.71 | 60 | 42.6 | 10.3 | 6.67 | 16.3732 | YES | 25
10 | 0.76 | 60 | 45.6 | 10.4 | 6.78 | 16.9807 | YES | 25
11 | 0.73 | 60 | 43.8 | 9.1 | 6.78 | 18.399 | YES | 25
12 | 0.73 | 60 | 43.8 | 10.1 | 6.76 | 17.1356 | YES | 25
13 | 0.49 | 60 | 29.4 | 10 | 6.7 | 16.46 | YES | 25
14 | 0.82 | 60 | 49.2 | 9.1 | 6.57 | 17.2917 | YES | 25
15 | 0.54 | 60 | 32.4 | 10.3 | 6.76 | 16.5707 | YES | 25
16 | 0.49 | 60 | 29.4 | 11 | 6.84 | 16.1965 | YES | 25
17 | 0.89 | 60 | 53.4 | 10.5 | 6.62 | 16.2095 | YES | 25
18 | 0.81 | 60 | 48.6 | 9.2 | 6.65 | 17.6381 | YES | 25
19 | 0.72 | 60 | 43.2 | 9.6 | 6.64 | 16.965 | YES | 25
20 | 0.53 | 60 | 31.8 | 10.4 | 6.7 | 16.1171 | YES | 25
21 | 0.59 | 60 | 35.4 | 10.2 | 6.73 | 16.5979 | YES | 25
22 | 0.62 | 60 | 37.2 | 11.2 | 6.76 | 15.7877 | YES | 25
23 | 0.65 | 60 | 39 | 11.2 | 6.48 | 14.4232 | YES | 25
24 | 0.76 | 60 | 45.6 | 11.4 | 6.58 | 14.9004 | YES | 25
25 | 0.73 | 60 | 43.8 | 11.9 | 6.55 | 14.2537 | YES | 25
26 | 0.75 | 60 | 45 | 13.1 | 6.76 | 13.7471 | YES | 25
27 | 0.78 | 60 | 46.8 | 11.8 | 6.6 | 14.6608 | YES | 25
28 | 0.9 | 60 | 54 | 12.2 | 6.69 | 14.9246 | YES | 25
29 | 0.86 | 60 | 51.6 | 11.4 | 6.62 | 15.2641 | YES | 25
30 | 0.77 | 60 | 46.2 | 11.2 | 6.65 | 15.463 | YES | 25
31 | 0.79 | 60 | 47.4 | 11.2 | 6.75 | 16.0271 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2