## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-04-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 1 | 7 | OK |  | 0.69
2 | 8 | 1 | 7 | OK |  | 0.67
3 | 8 | 1 | 7 | OK |  | 0.63
4 | 8 | 1 | 7 | OK |  | 0.48
5 | 9 | 1 | 8 | OK |  | 0.61
6 | 9 | 1 | 8 | OK |  | 0.42
7 | 9 | 1 | 8 | OK |  | 0.43
8 | 9 | 1 | 8 | OK |  | 0.43
9 | 9 | 1 | 8 | OK |  | 0.58
10 | 9 | 1 | 8 | OK |  | 0.35
11 | 9 | 1 | 8 | OK |  | 0.42
12 | 9 | 1 | 8 | OK |  | 0.37
13 | 9 | 1 | 8 | OK |  | 0.36
14 | 4 | 1 | 3 | OK |  | 0.25
15 | 4 | 1 | 3 | OK |  | 0.36
16 | 4 | 1 | 3 | OK |  | 0.24
17 | 6 | 1 | 5 | OK |  | 0.36
18 | 8 | 1 | 7 | OK |  | 0.39
19 | 8 | 1 | 7 | OK |  | 0.3
20 | 8 | 1 | 7 | OK |  | 0.27
21 | 8 | 1 | 7 | OK |  | 0.26
22 | 8 | 1 | 7 | OK |  | 0.23
23 | 4 | 1 | 3 | OK |  | 0.18
24 | 4 | 1 | 3 | OK |  | 0.18
25 | 4 | 1 | 3 | OK |  | 0.18
26 | 4 | 1 | 3 | OK |  | 0.13
27 | 4 | 1 | 3 | OK |  | 0.16
28 | 8 | 1 | 7 | OK |  | 0.19
29 | 8 | 1 | 7 | OK |  | 0.21
30 | 8 | 1 | 7 | OK |  | 0.23
31 |  |  |  | Change Filter
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2025-05-09
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.64 | 60 | 38.4 | 11.1 | 6.65 | 15.3441 | YES | 25
2 | 0.86 | 60 | 51.6 | 11 | 6.48 | 14.9362 | YES | 25
3 | 0.7 | 60 | 42 | 9.4 | 6.65 | 17.2043 | YES | 25
4 | 0.96 | 60 | 57.6 | 10.5 | 6.61 | 16.2781 | YES | 25
5 | 0.85 | 60 | 51 | 12.4 | 6.72 | 14.8076 | YES | 25
6 | 0.8 | 60 | 48 | 12.1 | 6.75 | 15.159 | YES | 25
7 | 0.92 | 60 | 55.2 | 12.4 | 6.72 | 14.9191 | YES | 25
8 | 0.86 | 60 | 51.6 | 12.1 | 6.75 | 15.2571 | YES | 25
9 | 1.03 | 60 | 61.8 | 11.5 | 6.7 | 15.8701 | YES | 25
10 | 0.93 | 60 | 55.8 | 11.8 | 6.75 | 15.6661 | YES | 25
11 | 0.63 | 60 | 37.8 | 11.5 | 6.86 | 16.0395 | YES | 25
12 | 0.43 | 60 | 25.8 | 11.6 | 6.83 | 15.4406 | YES | 25
13 | 0.51 | 60 | 30.6 | 12.6 | 6.88 | 14.4607 | YES | 25
14 | 0.5 | 60 | 30 | 11 | 6.63 | 15.1085 | YES | 25
15 | 0.48 | 60 | 28.8 | 12.8 | 6.76 | 13.5997 | YES | 25
16 | 0.58 | 60 | 34.8 | 12.4 | 6.76 | 14.5788 | YES | 25
17 | 0.54 | 60 | 32.4 | 12.7 | 6.91 | 14.575 | YES | 25
18 | 0.65 | 60 | 39 | 12 | 6.88 | 15.6792 | YES | 25
19 | 0.56 | 60 | 33.6 | 12.8 | 6.96 | 14.7828 | YES | 25
20 | 0.58 | 60 | 34.8 | 12.5 | 6.94 | 15.0046 | YES | 25
21 | 0.77 | 60 | 46.2 | 12.3 | 6.94 | 15.904 | YES | 25
22 | 0.74 | 60 | 44.4 | 11.7 | 6.8 | 15.7068 | YES | 25
23 | 0.78 | 60 | 46.8 | 11.5 | 6.76 | 15.7618 | YES | 25
24 | 0.75 | 60 | 45 | 12.7 | 6.8 | 14.3313 | YES | 25
25 | 0.76 | 60 | 45.6 | 12.1 | 6.78 | 15.2462 | YES | 25
26 | 1.5 | 60 | 90 | 13 | 6.88 | 15.7619 | YES | 25
27 | 0.46 | 60 | 27.6 | 12 | 6.96 | 15.7795 | YES | 25
28 | 0.63 | 60 | 37.8 | 12 | 6.75 | 14.9783 | YES | 25
29 | 0.77 | 60 | 46.2 | 12.2 | 6.8 | 15.269 | YES | 25
30 | 0.8 | 60 | 48 | 13.3 | 6.83 | 14.0016 | YES | 25
31 |  | 60 | [5 empty] | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2