## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-05-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 1 | 7 | OK |  | 0.17
2 | 8 | 1 | 7 | OK |  | 0.22
3 | 10 | 1 | 9 | OK |  | 0.19
4 | 12 | 1 | 11 | OK |  | 0.19
5 | 14 | 1 | 13 | OK |  | 0.12
6 | 14 | 1 | 13 | OK |  | 0.12
7 | 14 | 1 | 13 | OK |  | 0.17
8 | 18 | 1 | 17 | OK |  | 0.12
9 | 15 | 1 | 14 | OK |  | 0.2
10 | 15 | 1 | 14 | OK |  | 0.17
11 | 15 | 1 | 14 | OK |  | 0.2
12 | 2 | 1 | 1 | OK |  | 0.22
13 | 2 | 1 | 1 | OK |  | 0.26
14 | 4 | 1 | 3 | OK |  | 0.19
15 | 6 | 1 | 5 | OK |  | 0.26
16 | 6 | 1 | 5 | OK |  | 0.2
17 | 6 | 1 | 5 | OK |  | 0.18
18 | 6 | 1 | 5 | OK |  | 0.16
19 | 6 | 1 | 5 | OK |  | 0.17
20 | 7 | 1 | 6 | OK |  | 0.19
21 | 7 | 1 | 6 | OK |  | 0.34
22 | 7 | 1 | 6 | OK |  | 0.25
23 | 7 | 1 | 6 | OK |  | 0.23
24 | 7 | 1 | 6 | OK |  | 0.16
25 | 7 | 1 | 6 | OK |  | 0.19
26 | 7 | 1 | 6 | OK |  | 0.15
27 | 9 | 1 | 8 | OK |  | 0.17
28 | 9 | 1 | 8 | OK |  | 0.25
29 | 9 | 1 | 8 | OK |  | 0.21
30 | 9 | 1 | 8 | OK |  | 0.23
31 | 9 |  | 9 | OK |  | 0.3
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2025-06-09
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.87 | 60 | 52.2 | 12.1 | 6.74 | 15.2225 | YES | 25
2 | 1.02 | 60 | 61.2 | 13.4 | 6.65 | 13.3392 | YES | 25
3 | 0.99 | 60 | 59.4 | 13.6 | 6.95 | 14.6635 | YES | 25
4 | 1.06 | 60 | 63.6 | 12.9 | 6.98 | 15.6613 | YES | 25
5 | 1.17 | 60 | 70.2 | 11.8 | 6.7 | 15.8097 | YES | 25
6 | 1.19 | 60 | 71.4 | 13.5 | 6.61 | 13.3108 | YES | 25
7 | 0.54 | 60 | 32.4 | 13.5 | 6.71 | 12.825 | YES | 25
8 | 1.18 | 60 | 70.8 | 13.3 | 6.62 | 13.5251 | YES | 25
9 | 1.16 | 60 | 69.6 | 12.4 | 6.7 | 15.2067 | YES | 25
10 | 0.81 | 60 | 48.6 | 13.9 | 6.77 | 13.1686 | YES | 25
11 | 0.66 | 60 | 39.6 | 13.7 | 6.87 | 13.6164 | YES | 25
12 | 0.7 | 60 | 42 | 13.3 | 6.73 | 13.3373 | YES | 25
13 | 0.7 | 60 | 42 | 13.1 | 6.7 | 13.3672 | YES | 25
14 | 0.45 | 60 | 27 | 14 | 6.7 | 12.2288 | YES | 25
15 | 0.61 | 60 | 36.6 | 13.2 | 6.75 | 13.3887 | YES | 25
16 | 0.66 | 60 | 39.6 | 13.6 | 6.77 | 13.2073 | YES | 25
17 | 0.5 | 60 | 30 | 14.4 | 6.85 | 12.662 | YES | 25
18 | 0.47 | 60 | 28.2 | 13.8 | 6.9 | 13.3833 | YES | 25
19 | 0.53 | 60 | 31.8 | 14.4 | 6.62 | 11.6607 | YES | 25
20 | 0.52 | 60 | 31.2 | 14.3 | 6.72 | 12.172 | YES | 25
21 | 0.56 | 60 | 33.6 | 12.6 | 6.59 | 13.0573 | YES | 25
22 | 0.6 | 60 | 36 | 14.6 | 6.53 | 11.214 | YES | 25
23 | 0.62 | 60 | 37.2 | 13.9 | 6.7 | 12.5535 | YES | 25
24 | 0.64 | 60 | 38.4 | 14.6 | 6.92 | 13.0305 | YES | 25
25 | 0.63 | 60 | 37.8 | 14.4 | 6.85 | 12.8519 | YES | 25
26 | 0.62 | 60 | 37.2 | 15.3 | 6.93 | 12.4507 | YES | 25
27 | 0.66 | 60 | 39.6 | 15.3 | 6.71 | 11.5218 | YES | 25
28 | 0.66 | 60 | 39.6 | 14.6 | 6.61 | 11.6344 | YES | 25
29 | 0.63 | 60 | 37.8 | 15 | 6.65 | 11.4564 | YES | 25
30 | 0.67 | 60 | 40.2 | 15.2 | 6.78 | 11.9205 | YES | 25
31 | 1.23 | 60 | 73.8 | 15.3 | 6.78 | 12.6262 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2