## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-07-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 11 | 1 | 10 | OK |  | 0.13
2 | 11 | 1 | 10 | OK |  | 0.14
3 | 11 | 1 | 10 | OK |  | 0.12
4 | 11 | 1 | 10 | OK |  | 0.2
5 | 11 | 1 | 10 | OK |  | 0.12
6 | 11 | 1 | 10 | OK |  | 0.17
7 | 12 | 1 | 11 | OK |  | 0.09
8 | 12 | 1 | 11 | OK |  | 0.12
9 | 12 | 1 | 11 | OK |  | 0.12
10 | 14 | 1 | 13 | OK |  | 0.16
11 | 14 | 1 | 13 | OK |  | 0.15
12 | 14 | 1 | 13 | OK |  | 0.21
13 | 14 | 1 | 13 | OK |  | 0.21
14 | 15 | 1 | 14 | OK |  | 0.1
15 | 15 | 1 | 14 | OK |  | 0.18
16 | 15 | 1 | 14 | OK |  | 0.12
17 | 15 | 1 | 14 | OK |  | 0.11
18 | 15 | 1 | 14 | OK |  | 0.21
19 | 15 | 1 | 14 | OK |  | 0.17
20 | 15 | 1 | 14 | OK |  | 0.11
21 | 16 | 1 | 15 | OK |  | 0.1
22 | 16 | 1 | 15 | OK |  | 0.1
23 | 16 | 1 | 15 | OK |  | 0.09
24 | 16 | 1 | 15 | OK |  | 0.17
25 | 16 | 1 | 15 | OK |  | 0.23
26 | 17 | 1 | 16 | OK |  | 0.11
27 | 17 | 1 | 16 | OK |  | 0.1
28 | 17 | 1 | 16 | OK |  | 0.12
29 | 18 | 1 | 17 | OK |  | 0.15
30 | 18 | 1 | 17 | OK |  | 0.13
31 | 18 | 1 | 17 | OK |  | 0.14
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Giovanni Rangel
[5 empty] | SIGNATURE: Giovanni Rangel |  | 2025-09-10
[5 empty] | PHONE #: (541) 373-9150 |  | CERT# T1D1-859079
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-07-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.63 | 60 | 37.8 | 20.3 | 6.73 | 8.2451 | YES | 25
2 | 1.15 | 60 | 69 | 20.4 | 6.75 | 8.7659 | YES | 25
3 | 1.07 | 60 | 64.2 | 20.2 | 6.65 | 8.4772 | YES | 25
4 | 0.98 | 60 | 58.8 | 21.2 | 6.67 | 7.895 | YES | 25
5 | 0.85 | 60 | 51 | 20.3 | 6.58 | 7.9917 | YES | 25
6 | 0.76 | 60 | 45.6 | 20.4 | 6.59 | 7.8842 | YES | 25
7 | 0.98 | 60 | 58.8 | 22.8 | 6.7 | 7.1563 | YES | 25
8 | 1.24 | 60 | 74.4 | 22.4 | 6.6 | 7.2996 | YES | 25
9 | 0.95 | 60 | 57 | 22.8 | 6.93 | 7.7839 | YES | 25
10 | 0.75 | 60 | 45 | 24.3 | 6.86 | 6.6783 | YES | 25
11 | 1.05 | 60 | 63 | 23 | 6.78 | 7.3373 | YES | 25
12 | 0.51 | 60 | 30.6 | 24.3 | 6.72 | 6.152 | YES | 25
13 | 0.99 | 60 | 59.4 | 24.1 | 6.66 | 6.4513 | YES | 25
14 | 0.95 | 60 | 57 | 24 | 6.68 | 6.5153 | YES | 25
15 | 0.94 | 60 | 56.4 | 16.9 | 7.1 | 12.3596 | YES | 25
16 | 1.12 | 60 | 67.2 | 15.7 | 6.65 | 11.5624 | YES | 25
17 | 1.11 | 60 | 66.6 | 15.5 | 6.85 | 12.6125 | YES | 25
18 | 1.11 | 60 | 66.6 | 15.6 | 6.9 | 12.7638 | YES | 25
19 | 0.96 | 60 | 57.6 | 16.2 | 6.75 | 11.3941 | YES | 25
20 | 0.98 | 60 | 58.8 | 16.4 | 6.84 | 11.6531 | YES | 25
21 | 1.05 | 60 | 63 | 16 | 6.96 | 12.6197 | YES | 25
22 | 1.01 | 60 | 60.6 | 15.7 | 6.97 | 12.8652 | YES | 25
23 | 0.92 | 60 | 55.2 | 15.9 | 6.95 | 12.4702 | YES | 25
24 | 0.96 | 60 | 57.6 | 15.7 | 6.92 | 12.5556 | YES | 25
25 | 0.81 | 60 | 48.6 | 16.1 | 6.75 | 11.2749 | YES | 25
26 | 0.98 | 60 | 58.8 | 16 | 6.78 | 11.7056 | YES | 25
27 | 1 | 60 | 60 | 15.9 | 6.82 | 11.9894 | YES | 25
28 | 0.9 | 60 | 54 | 16.2 | 6.86 | 11.7907 | YES | 25
29 | 0.88 | 60 | 52.8 | 16.4 | 6.72 | 11.0143 | YES | 25
30 | 0.93 | 60 | 55.8 | 15.9 | 6.75 | 11.5865 | YES | 25
31 | 0.83 | 60 | 49.8 | 16.8 | 6.88 | 11.3176 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2