## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41 | 94489 | WTP ID: TP- | A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 16 | 1 | 15 | OK |  | 0.1 | 0.1
2 | 19 | 1 | 18 | OK |  | 0.12 | 0.12
3 | 15 | 1 | 14 | OK |  | 0.13 | 0.13
4 | 15 | 1 | 14 | OK |  | 0.16 | 0.16
5 | 19 | 1 | 18 | OK |  | 0.13 | 0.13
6 | 19 | 1 | 18 | OK |  | 0.16 | 0.16
7 | 20 | 1 | 19 | OK |  | 0.15 | 0.15
8 | 20 | 1 | 19 | OK |  | 0.27 | 0.27
9 | 20 | 1 | 19 | OK |  | 0.49 | 0.49
10 | 28 | 1 | 27 | OK |  | 0.2 | 0.2
11 | 28 | 1 | 27 | OK |  | 0.3 | 0.3
12 | 19 | 1 | 18 | OK |  | 0.13 | 0.13
13 | 19 | 1 | 18 | OK |  | 0.16 | 0.16
14 | 16 | 1 | 15 | OK |  | 0.16 | 0.16
15 | 16 | 1 | 15 | OK |  | 0.15 | 0.15
16 | 14 | 1 | 13 | OK |  | 0.19 | 0.19
17 | 13 | 1 | 12 | OK |  | 0.1 | 0.1
18 | 13 | 1 | 12 | OK |  | 0.15 | 0.15
19 | 13 | 1 | 12 | OK |  | 0.14 | 0.14
20 | 13 | 1 | 12 | OK |  | 0.15 | 0.15
21 | 13 | 1 | 12 | OK |  | 0.11 | 0.11
22 | 13 | 1 | 12 | OK |  | 0.14 | 0.14
23 | 12 | 1 | 11 | OK |  | 0.15 | 0.15
24 | 13 | 1 | 12 | OK |  | 0.12 | 0.12
25 | 13 | 1 | 12 | OK |  | 0.14 | 0.14
26 | 12 | 1 | 11 | OK |  | 0.14 | 0.14
27 | 12 | 1 | 11 | OK |  | 0.16 | 0.16
28 | 12 | 1 | 11 | OK |  | 0.14 | 0.14
29 | 12 | 1 | 11 | OK |  | 0.16 | 0.16
30 | 12 | 1 | 11 | OK |  | 0.12 | 0.12
31 | 12 | 1 | 11 | OK |  | 0.16 | 0.16
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Giovanni Rangel
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 9/10/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 373-9150 |  | CERT #:T1D1-859079
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  | ID#: 41 | 94489 | Month/Year: | 2025-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.98 | 60 | 58.8 | 16.5 | 6.84 | 23.1499 | YES | 25
2 | 1.01 | 60 | 60.6 | 16.9 | 6.73 | 21.7006 | YES | 25
3 | 1.05 | 60 | 63 | 16.6 | 6.7 | 21.9977 | YES | 25
4 | 1.12 | 60 | 67.2 | 16.3 | 6.73 | 22.8837 | YES | 25
5 | 0.96 | 60 | 57.6 | 16 | 6.88 | 24.246 | YES | 25
6 | 0.86 | 60 | 51.6 | 16.8 | 6.77 | 21.7974 | YES | 25
7 | 0.89 | 60 | 53.4 | 17.4 | 6.84 | 21.5634 | YES | 25
8 | 0.95 | 60 | 57 | 17.9 | 7.12 | 23.3123 | YES | 25
9 | 0.68 | 60 | 40.8 | 17.7 | 7.19 | 23.5134 | YES | 25
10 | 0.85 | 60 | 51 | 17.5 | 7.15 | 23.9411 | YES | 25
11 | 0.78 | 60 | 46.8 | 16.2 | 7.01 | 24.5981 | YES | 25
12 | 0.58 | 60 | 34.8 | 16.6 | 6.89 | 22.3754 | YES | 25
13 | 0.67 | 60 | 40.2 | 17.7 | 7.07 | 22.4561 | YES | 25
14 | 0.57 | 60 | 34.2 | 17.7 | 6.91 | 20.9075 | YES | 25
15 | 0.57 | 60 | 34.2 | 16.5 | 7.18 | 25.0742 | YES | 25
16 | 0.54 | 60 | 32.4 | 17.8 | 6.95 | 21.0078 | YES | 25
17 | 0.7 | 60 | 42 | 17.1 | 6.97 | 22.6015 | YES | 25
18 | 0.67 | 60 | 40.2 | 16.5 | 6.85 | 22.423 | YES | 25
19 | 0.63 | 60 | 37.8 | 15.8 | 7.01 | 24.8368 | YES | 25
20 | 0.63 | 60 | 37.8 | 16.2 | 7.16 | 25.5692 | YES | 25
21 | 0.74 | 60 | 44.4 | 16.5 | 6.5 | 19.8244 | YES | 25
22 | 0.62 | 60 | 37.2 | 16.8 | 6.66 | 20.3457 | YES | 25
23 | 0.74 | 60 | 44.4 | 16.8 | 6.88 | 22.4021 | YES | 25
24 | 0.54 | 60 | 32.4 | 16.7 | 6.86 | 21.876 | YES | 25
25 | 0.73 | 60 | 43.8 | 16.6 | 6.91 | 22.9357 | YES | 25
26 | 0.73 | 60 | 43.8 | 16.6 | 6.91 | 22.9357 | YES | 25
27 | 0.79 | 60 | 47.4 | 16.9 | 7.03 | 23.6708 | YES | 25
28 | 0.82 | 60 | 49.2 | 16.5 | 6.93 | 23.5056 | YES | 25
29 | 0.83 | 60 | 49.8 | 16.8 | 7.11 | 24.6655 | YES | 25
30 | 0.57 | 60 | 34.2 | 15.8 | 6.84 | 23.1497 | YES | 25
31 | 0.83 | 60 | 49.8 | 15.9 | 6.89 | 24.138 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2