## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-02-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: A-Lower Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 1 | 19 | OK | 0.11 | 0.11
2 | 20 | 1 | 19 | OK | 0.17 | 0.17
3 | 16 | 1 | 15 | OK | 0.12 | 0.12
4 | 17 | 1 | 16 | OK | 0.14 | 0.14
5 | 17 | 1 | 16 | OK | 0.15 | 0.15
6 | 17 | 1 | 16 | OK | 0.17 | 0.17
7 | 18 | 1 | 17 | OK | 0.11 | 0.11
8 | 19 | 1 | 18 | OK | 0.22 | 0.22
9 | 20 | 1 | 19 | OK | 0.16 | 0.16
10 | 20 | 1 | 19 | OK | 0.19 | 0.19
11 | 18 | 1 | 17 | OK | 0.27 | 0.27
12 | 18 | 1 | 17 | OK | 0.21 | 0.21
13 | 17 | 1 | 16 | OK | 0.16 | 0.16
14 | 17 | 1 | 16 | OK | 0.17 | 0.17
15 | 17 | 1 | 16 | OK | 0.14 | 0.14
16 | 17 | 1 | 16 | OK | 0.12 | 0.12
17 | 17 | 1 | 16 | OK | 0.15 | 0.15
18 | 18 | 1 | 17 | OK | 0.13 | 0.13
19 | 20 | 1 | 19 | OK | 0.14 | 0.14
20 | 16 | 1 | 15 | OK | 0.23 | 0.23
21 | 16 | 1 | 15 | OK | 0.23 | 0.23
22 | 16 | 1 | 15 | OK | 0.21 | 0.21
23 | 20 | 1 | 19 | OK | 0.23 | 0.23
24 | 20 | 1 | 19 | OK | 0.25 | 0.25
25 | 20 | 1 | 19 | OK | 0.29 | 0.29
26 | 22 | 1 | 21 | OK | 0.28 | 0.28
27 | 22 | 1 | 21 | OK | 0.25 | 0.25
28 | 13 | 1 | 12 | OK | 0.26 | 0.26
29 |  | 1 |  | Change Filter
30 |  | 1 |  | Change Filter
31 |  | 1 |  | Change Filter
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Giovanni Rangel
SIGNATURE: Giovanni Rangel
[5 empty] | PHONE #: (541) 373- 9150 |  | CERT# T1D1- 859079
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: A-Lower Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2026-02-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.74 | 60 | 44.4 | 11.7 | 7.04 | 17.0364 | YES | 25
2 | 0.7 | 60 | 42 | 10.8 | 7.08 | 18.2185 | YES | 25
3 | 0.62 | 60 | 37.2 | 10.3 | 7 | 18.1443 | YES | 25
4 | 0.68 | 60 | 40.8 | 11.1 | 7.02 | 17.468 | YES | 25
5 | 0.93 | 60 | 55.8 | 10.5 | 7 | 18.536 | YES | 25
6 | 0.73 | 60 | 43.8 | 11.8 | 7.04 | 16.9094 | YES | 25
7 | 0.84 | 60 | 50.4 | 11.5 | 6.98 | 17.0926 | YES | 25
8 | 0.95 | 60 | 57 | 11.3 | 7 | 17.6435 | YES | 25
9 | 0.91 | 60 | 54.6 | 10.5 | 6.92 | 17.9933 | YES | 25
10 | 0.63 | 60 | 37.8 | 10.4 | 6.83 | 17.0284 | YES | 25
11 | 0.7 | 60 | 42 | 10.8 | 6.81 | 16.6134 | YES | 25
12 | 0.6 | 60 | 36 | 10.6 | 6.75 | 16.3087 | YES | 25
13 | 0.66 | 60 | 39.6 | 10.7 | 6.7 | 16.0382 | YES | 25
14 | 0.72 | 60 | 43.2 | 11 | 6.84 | 16.6071 | YES | 25
15 | 0.7 | 60 | 42 | 11.1 | 6.86 | 16.5779 | YES | 25
16 | 0.72 | 60 | 43.2 | 10.8 | 6.91 | 17.226 | YES | 25
17 | 0.75 | 60 | 45 | 9.9 | 6.99 | 18.8244 | YES | 25
18 | 0.47 | 60 | 28.2 | 9.4 | 7.01 | 18.9801 | YES | 25
19 | 0.75 | 60 | 45 | 8.9 | 6.96 | 19.881 | YES | 25
20 | 0.57 | 60 | 34.2 | 8.8 | 6.97 | 19.6812 | YES | 25
21 | 0.59 | 60 | 35.4 | 10 | 6.89 | 17.7543 | YES | 25
22 | 0.55 | 60 | 33 | 11.2 | 6.93 | 16.595 | YES | 25
23 | 0.68 | 60 | 40.8 | 11.5 | 6.7 | 15.2815 | YES | 25
24 | 0.71 | 60 | 42.6 | 11.8 | 6.59 | 14.5033 | YES | 25
25 | 0.86 | 60 | 51.6 | 11.9 | 6.51 | 14.2621 | YES | 25
26 | 0.8 | 60 | 48 | 10.7 | 6.43 | 14.8717 | YES | 25
27 | 0.81 | 60 | 48.6 | 11.7 | 6.44 | 14.035 | YES | 25
28 | 0.76 | 60 | 45.6 | 12.1 | 6.48 | 13.8003 | YES | 25
29 |  | 60 | [5 empty] | 25
30 |  | 60 | [5 empty] | 25
31 |  | 60 | [5 empty] | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2