## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-07-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 28 | 0 | 28 | Change Filter | 0.14
2 | 40 | 1 | 39 | Change Filter | 0.17
3 | 28 | 0 | 28 | Change Filter | 0.14
4 | 27 | 0 | 27 | OK | 0.21
5 | 29 | 0 | 29 | Change Filter | 0.15
6 | 29 | 1 | 28 | Change Filter | 0.1
7 | 33 | 1 | 32 | Change Filter | 0.1
8 | 32 | 1 | 31 | Change Filter | 0.1
9 | 37 | 1 | 36 | Change Filter | 0.16
10 | 38 | 1 | 37 | Change Filter | 0.14
11 | 36 | 1 | 35 | Change Filter | 0.09
12 | 36 | 1 | 35 | Change Filter | 0.16
13 | 39 | 1 | 38 | Change Filter | 0.16
14 | 42 | 1 | 41 | Change Filter | 0.17
15 | 46 | 1 | 45 | Change Filter | 0.11
16 | 26 | 1 | 25 | OK | 0.13
17 | 28 | 1 | 27 | OK | 0.19
18 | 27 | 1 | 26 | OK | 0.19
19 | 27 | 1 | 26 | OK | 0.22
20 | 28 | 1 | 27 | OK | 0.11
21 | 29 | 1 | 28 | Change Filter | 0.15
22 | 29 | 1 | 28 | Change Filter | 0.14
23 | 29 | 1 | 28 | Change Filter | 0.16
24 | 32 | 1 | 31 | Change Filter | 0.18
25 | 32 | 1 | 31 | Change Filter | 0.15
26 | 32 | 1 | 31 | Change Filter | 0.09
27 | 34 | 1 | 33 | Change Filter | 0.11
28 | 26 | 1 | 25 | OK | 0.18
29 | 33 | 1 | 32 | Change Filter | 0.23
30 | 30 | 1 | 29 | Change Filter | 0.21
31 | 34 | 1 | 33 | Change Filter | 0.16
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-08-07
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-07-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.57 | 132 | 75.24 | 12.4 | 7 | 15.781 | YES | 25
2 | 2.04 | 132 | 269.28 | 14.4 | 7.04 | 16.1994 | YES | 25
3 | 1.42 | 132 | 187.44 | 14.2 | 7.1 | 15.6417 | YES | 25
4 | 1.47 | 132 | 194.04 | 16.4 | 7.05 | 13.3303 | YES | 25
5 | 0.79 | 132 | 104.28 | 13.4 | 6.89 | 14.2055 | YES | 25
6 | 1.45 | 132 | 191.4 | 15.7 | 6.95 | 13.4293 | YES | 25
7 | 1.22 | 132 | 161.04 | 15.1 | 6.97 | 13.7186 | YES | 25
8 | 0.58 | 132 | 76.56 | 13.2 | 7.1 | 15.1948 | YES | 25
9 | 0.3 | 132 | 39.6 | 13.9 | 7.02 | 13.6331 | YES | 25
10 | 0.36 | 132 | 47.52 | 13.3 | 6.99 | 14.1308 | YES | 25
11 | 0.22 | 132 | 29.04 | 13 | 6.99 | 14.1884 | YES | 25
12 | 0.34 | 132 | 44.88 | 13.4 | 7 | 14.0567 | YES | 25
13 | 0.25 | 132 | 33 | 12.3 | 6.98 | 15.239 | YES | 25
14 | 0.47 | 132 | 62.04 | 13.6 | 6.85 | 13.3138 | YES | 25
15 | 1.17 | 132 | 154.44 | 13.2 | 6.99 | 15.6022 | YES | 25
16 | 1.35 | 132 | 178.2 | 13 | 7.1 | 16.8094 | YES | 25
17 | 0.31 | 132 | 40.92 | 12.9 | 7.1 | 15.0323 | YES | 25
18 | 1.02 | 132 | 134.64 | 13 | 7.04 | 15.8345 | YES | 25
19 | 1.05 | 132 | 138.6 | 12.9 | 7.1 | 16.3541 | YES | 25
20 | 1.3 | 132 | 171.6 | 13.9 | 6.99 | 15.1124 | YES | 25
21 | 1.03 | 132 | 135.96 | 13.8 | 7.01 | 14.8623 | YES | 25
22 | 0.49 | 132 | 64.68 | 13.9 | 6.93 | 13.4739 | YES | 25
23 | 0.64 | 132 | 84.48 | 13.2 | 7.3 | 16.475 | YES | 25
24 | 0.34 | 132 | 44.88 | 13.6 | 7 | 13.8698 | YES | 25
25 | 0.43 | 132 | 56.76 | 13.6 | 7.06 | 14.329 | YES | 25
26 | 0.4 | 132 | 52.8 | 13 | 7.07 | 14.9193 | YES | 25
27 | 1.68 | 132 | 221.76 | 13.3 | 7.13 | 17.2976 | YES | 25
28 | 0.3 | 132 | 39.6 | 13 | 7.14 | 15.1381 | YES | 25
29 | 0.62 | 132 | 81.84 | 12.9 | 7.07 | 15.4007 | YES | 25
30 | 0.47 | 132 | 62.04 | 15 | 7 | 12.8174 | YES | 25
31 | 0.57 | 132 | 75.24 | 13.8 | 7.1 | 14.5813 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2