## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-08-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 35 | 1 | 34 | Change Filter | 0.17
2 | 26 | 1 | 25 | OK | 0.29
3 | 26 | 1 | 25 | OK | 0.16
4 | 27 | 1 | 26 | OK | 0.09
5 | 27 | 1 | 26 | OK | 0.08
6 | 28 | 1 | 27 | OK | 0.1
7 | 27 | 1 | 26 | OK | 0.16
8 | 27 | 1 | 26 | OK | 0.12
9 | 29 | 1 | 28 | Change Filter | 0.29
10 | 32 | 1 | 31 | Change Filter | 0.08
11 | 39 | 1 | 38 | Change Filter | 0.12
12 | 28 | 1 | 27 | OK | 0.14
13 | 28 | 1 | 27 | OK | 0.08
14 | 27 | 1 | 26 | OK | 0.08
15 | 27 | 1 | 26 | OK | 0.22
16 | 30 | 1 | 29 | Change Filter | 0.1
17 | 33 | 1 | 32 | Change Filter | 0.09
18 | 27 | 1 | 26 | OK | 0.1
19 | 27 | 1 | 26 | OK | 0.09
20 | 28 | 1 | 27 | OK | 0.12
21 | 29 | 1 | 28 | Change Filter | 0.17
22 | 33 | 1 | 32 | Change Filter | 0.12
23 | 35 | 1 | 34 | Change Filter | 0.09
24 | 27 | 1 | 26 | OK | 0.33
25 | 27 | 1 | 26 | OK | 0.11
26 | 28 | 1 | 27 | OK | 0.08
27 | 28 | 1 | 27 | OK | 0.12
28 | 28 | 1 | 27 | OK | 0.13
29 | 29 | 1 | 28 | Change Filter | 0.12
30 | 30 | 1 | 29 | Change Filter | 0.16
31 | 30 | 1 | 29 | Change Filter | 0.1
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-09-05
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-08-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.47 | 132 | 62.04 | 14 | 7.1 | 14.2244 | YES | 25
2 | 0.56 | 132 | 73.92 | 14.3 | 7.11 | 14.1383 | YES | 25
3 | 0.4 | 132 | 52.8 | 14.3 | 6.96 | 13.129 | YES | 25
4 | 0.36 | 132 | 47.52 | 13.8 | 7.03 | 13.8705 | YES | 25
5 | 0.46 | 132 | 60.72 | 14.2 | 7.1 | 14.0194 | YES | 25
6 | 1.88 | 132 | 248.16 | 13.3 | 7.02 | 16.9902 | YES | 25
7 | 1.6 | 132 | 211.2 | 13.6 | 7.1 | 16.6168 | YES | 25
8 | 0.88 | 132 | 116.16 | 13.1 | 6.85 | 14.4271 | YES | 25
9 | 0.78 | 132 | 102.96 | 13.5 | 7.14 | 15.4645 | YES | 25
10 | 0.57 | 132 | 75.24 | 13.5 | 6.91 | 13.8633 | YES | 25
11 | 0.5 | 132 | 66 | 13.8 | 6.97 | 13.7834 | YES | 25
12 | 0.47 | 132 | 62.04 | 13.4 | 7.05 | 14.5342 | YES | 25
13 | 0.69 | 132 | 91.08 | 13.4 | 7.14 | 15.4092 | YES | 25
14 | 0.93 | 132 | 122.76 | 14.2 | 6.95 | 13.9908 | YES | 25
15 | 0.95 | 132 | 125.4 | 14.2 | 7.13 | 14.9917 | YES | 25
16 | 0.66 | 132 | 87.12 | 13.2 | 7.05 | 15.0523 | YES | 25
17 | 0.8 | 132 | 105.6 | 13.8 | 7.04 | 14.6394 | YES | 25
18 | 1.33 | 132 | 175.56 | 14.3 | 6.98 | 14.7099 | YES | 25
19 | 0.61 | 132 | 80.52 | 13 | 7.01 | 14.9447 | YES | 25
20 | 1.14 | 132 | 150.48 | 13 | 6.95 | 15.5261 | YES | 25
21 | 0.53 | 132 | 69.96 | 14.1 | 6.96 | 13.5055 | YES | 25
22 | 0.64 | 132 | 84.48 | 13.7 | 6.97 | 14.0997 | YES | 25
23 | 0.47 | 132 | 62.04 | 13.7 | 7.05 | 14.2456 | YES | 25
24 | 0.23 | 132 | 30.36 | 14.2 | 6.93 | 12.8186 | YES | 25
25 | 0.29 | 132 | 38.28 | 14 | 6.98 | 13.3269 | YES | 25
26 | 0.54 | 132 | 71.28 | 13.5 | 7.02 | 14.392 | YES | 25
27 | 0.66 | 132 | 87.12 | 13.5 | 7 | 14.4826 | YES | 25
28 | 0.62 | 132 | 81.84 | 13.4 | 7.1 | 15.0618 | YES | 25
29 | 0.53 | 132 | 69.96 | 13.6 | 7.06 | 14.4934 | YES | 25
30 | 0.75 | 132 | 99 | 12.6 | 6.9 | 14.9728 | YES | 25
31 | 0.68 | 132 | 89.76 | 13 | 6.98 | 14.8977 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2