## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-09-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 31 | 1 | 30 | Change Filter | 0.08
2 | 31 | 1 | 30 | Change Filter | 0.1
3 | 33 | 1 | 32 | Change Filter | 0.08
4 | 34 | 1 | 33 | Change Filter | 0.11
5 | 35 | 1 | 34 | Change Filter | 0.1
6 | 27 | 1 | 26 | OK | 0.12
7 | 27 | 1 | 26 | OK | 0.09
8 | 27 | 1 | 26 | OK | 0.1
9 | 28 | 1 | 27 | OK | 0.08
10 | 28 | 1 | 27 | OK | 0.13
11 | 28 | 1 | 27 | OK | 0.19
12 | 28 | 1 | 27 | OK | 0.21
13 | 29 | 1 | 28 | Change Filter | 0.15
14 | 30 | 1 | 29 | Change Filter | 0.33
15 | 37 | 1 | 36 | Change Filter | 0.1
16 | 36 | 1 | 35 | Change Filter | 0.09
17 | 29 | 1 | 28 | Change Filter | 0.12
18 | 28 | 1 | 27 | OK | 0.17
19 | 30 | 1 | 29 | Change Filter | 0.17
20 | 31 | 1 | 30 | Change Filter | 0.11
21 | 31 | 1 | 30 | Change Filter | 0.12
22 | 32 | 1 | 31 | Change Filter | 0.13
23 | 34 | 1 | 33 | Change Filter | 0.24
24 | 28 | 1 | 27 | OK | 0.13
25 | 28 | 1 | 27 | OK | 0.11
26 | 29 | 1 | 28 | Change Filter | 0.17
27 | 32 | 1 | 31 | Change Filter | 0.08
28 | 34 | 1 | 33 | Change Filter | 0.1
29 | 32 | 1 | 31 | Change Filter | 0.07
30 | 39 | 1 | 38 | Change Filter | 0.14
31 |  |  |  | Change Filter
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-10-06
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.68 | 132 | 89.76 | 12.8 | 6.98 | 15.098 | YES | 25
2 | 0.26 | 132 | 34.32 | 14.1 | 7.03 | 13.4402 | YES
3 | 0.68 | 132 | 89.76 | 13.5 | 7.01 | 14.5696 | YES
4 | 0.55 | 132 | 72.6 | 14.2 | 7.06 | 13.9553 | YES
5 | 0.36 | 132 | 47.52 | 14.3 | 7.05 | 13.5141 | YES
6 | 0.5 | 132 | 66 | 13.1 | 6.9 | 14.0734 | YES
7 | 0.22 | 132 | 29.04 | 14.1 | 6.96 | 13.0348 | YES
8 | 0.65 | 132 | 85.8 | 13.9 | 6.94 | 13.7738 | YES
9 | 0.68 | 132 | 89.76 | 13 | 6.83 | 14.091 | YES
10 | 0.4 | 132 | 52.8 | 13.1 | 7 | 14.44 | YES
11 | 0.89 | 132 | 117.48 | 13.4 | 6.97 | 14.8016 | YES
12 | 0.53 | 132 | 69.96 | 13.3 | 6.9 | 13.9341 | YES
13 | 0.64 | 132 | 84.48 | 13.5 | 6.93 | 14.0788 | YES
14 | 0.48 | 132 | 63.36 | 13.3 | 6.86 | 13.6502 | YES
15 | 0.67 | 132 | 88.44 | 13.3 | 6.86 | 13.9499 | YES
16 | 0.55 | 132 | 72.6 | 13.2 | 6.86 | 13.8523 | YES
17 | 1.68 | 132 | 221.76 | 12.9 | 6.85 | 16.0169 | YES
18 | 1.01 | 132 | 133.32 | 13.6 | 6.95 | 14.697 | YES
19 | 1.43 | 132 | 188.76 | 12.5 | 6.91 | 16.3472 | YES
20 | 0.79 | 132 | 104.28 | 13.4 | 6.95 | 14.5255 | YES
21 | 0.62 | 132 | 81.84 | 13.4 | 6.9 | 13.9842 | YES
22 | 0.53 | 132 | 69.96 | 13.8 | 7 | 13.9858 | YES
23 | 0.55 | 132 | 72.6 | 14.2 | 7.03 | 13.8006 | YES
24 | 0.69 | 132 | 91.08 | 14.7 | 6.89 | 12.8732 | YES
25 | 0.5 | 132 | 66 | 13.7 | 6.91 | 13.5699 | YES
26 | 0.48 | 132 | 63.36 | 12.9 | 6.93 | 14.3898 | YES
27 | 0.62 | 132 | 81.84 | 13.6 | 6.91 | 13.8497 | YES
28 | 0.56 | 132 | 73.92 | 14 | 6.93 | 13.4916 | YES
29 | 0.59 | 132 | 77.88 | 12.3 | 6.93 | 15.545 | YES
30 | 0.44 | 132 | 58.08 | 13.2 | 6.86 | 13.6792 | YES
31 |  | 132
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2