## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-10-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 12 | 1 | 11 | OK | 0.13 | 0.13
2 | 12 | 1 | 11 | OK | 0.13 | 0.13
3 | 13 | 1 | 12 | OK | 0.13 | 0.13
4 | 13 | 1 | 12 | OK | 0.12 | 0.12
5 | 13 | 1 | 12 | OK | 0.16 | 0.16
6 | 13 | 1 | 12 | OK | 0.14 | 0.14
7 | 13 | 1 | 12 | OK | 0.18 | 0.18
8 | 13 | 1 | 12 | OK | 0.08 | 0.08
9 | 14 | 1 | 13 | OK | 0.18 | 0.18
10 | 14 | 1 | 13 | OK | 0.09 | 0.09
11 | 14 | 1 | 13 | OK | 0.12 | 0.12
12 | 15 | 1 | 14 | OK | 0.1 | 0.1
13 | 15 | 1 | 14 | OK | 0.07 | 0.07
14 | 15 | 1 | 14 | OK | 0.13 | 0.13
15 | 14 | 1 | 13 | OK | 0.07 | 0.07
16 | 14 | 1 | 13 | OK | 0.08 | 0.08
17 | 14 | 1 | 13 | OK | 0.09 | 0.09
18 | 14 | 1 | 13 | OK | 0.1 | 0.1
19 | 14 | 1 | 13 | OK | 0.15 | 0.15
20 | 14 | 1 | 13 | OK | 0.19 | 0.19
21 | 14 | 1 | 13 | OK | 0.18 | 0.18
22 | 14 | 1 | 13 | OK | 0.1 | 0.1
23 | 16 | 1 | 15 | OK | 0.12 | 0.12
24 | 16 | 1 | 15 | OK | 0.14 | 0.14
25 | 16 | 1 | 15 | OK | 0.12 | 0.12
26 | 16 | 1 | 15 | OK | 0.09 | 0.09
27 | 16 | 1 | 15 | OK | 0.09 | 0.09
28 | 16 | 1 | 15 | OK | 0.13 | 0.13
29 | 16 | 1 | 15 | OK | 0.13 | 0.13
30 | 16 | 1 | 15 | OK | 0.1 | 0.1
31 | 16 | 1 | 15 | OK | 0.16 | 0.16
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-11-05
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-10-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.45 | 132 | 59.4 | 14 | 7 | 13.6743 | YES | 25
2 | 0.36 | 132 | 47.52 | 13.3 | 6.95 | 13.9223 | YES | 25
3 | 0.51 | 132 | 67.32 | 13.7 | 6.94 | 13.7378 | YES | 25
4 | 0.44 | 132 | 58.08 | 12.7 | 7.03 | 15.0656 | YES | 25
5 | 0.4 | 132 | 52.8 | 15 | 6.96 | 12.5269 | YES | 25
6 | 0.63 | 132 | 83.16 | 13.8 | 6.87 | 13.4792 | YES | 25
7 | 0.55 | 132 | 72.6 | 13.6 | 6.94 | 13.8934 | YES | 25
8 | 0.73 | 132 | 96.36 | 13.3 | 6.87 | 14.0981 | YES | 25
9 | 1 | 132 | 132 | 13.6 | 6.92 | 14.5178 | YES | 25
10 | 0.65 | 132 | 85.8 | 12.7 | 6.92 | 14.8139 | YES | 25
11 | 0.52 | 132 | 68.64 | 12.4 | 7.03 | 15.8553 | YES | 25
12 | 0.56 | 132 | 73.92 | 14.3 | 6.92 | 13.174 | YES | 25
13 | 0.65 | 132 | 85.8 | 13.7 | 6.88 | 13.6515 | YES | 25
14 | 0.77 | 132 | 101.64 | 12.8 | 6.96 | 15.141 | YES | 25
15 | 0.73 | 132 | 96.36 | 14 | 7.01 | 14.1714 | YES | 25
16 | 0.68 | 132 | 89.76 | 14.3 | 6.95 | 13.506 | YES | 25
17 | 0.41 | 132 | 54.12 | 13.9 | 6.95 | 13.4509 | YES | 25
18 | 0.53 | 132 | 69.96 | 12.5 | 6.95 | 14.9748 | YES | 25
19 | 1.9 | 132 | 250.8 | 13.8 | 6.94 | 15.9908 | YES | 25
20 | 0.65 | 132 | 85.8 | 13.7 | 6.99 | 14.221 | YES | 25
21 | 0.2 | 132 | 26.4 | 13.4 | 6.92 | 13.4282 | YES | 25
22 | 0.3 | 132 | 39.6 | 11 | 6.96 | 16.5231 | YES | 25
23 | 0.24 | 132 | 31.68 | 12.3 | 6.94 | 15.0203 | YES | 25
24 | 0.82 | 132 | 108.24 | 12 | 6.85 | 15.8097 | YES | 25
25 | 1.15 | 132 | 151.8 | 12.9 | 6.99 | 15.8813 | YES | 25
26 | 0.79 | 132 | 104.28 | 14 | 6.92 | 13.7996 | YES | 25
27 | 0.52 | 132 | 68.64 | 13.6 | 6.85 | 13.3902 | YES | 25
28 | 0.42 | 132 | 55.44 | 12.3 | 6.83 | 14.7612 | YES | 25
29 | 0.35 | 132 | 46.2 | 11.2 | 6.85 | 15.805 | YES | 25
30 | 1.54 | 132 | 203.28 | 12.1 | 7.05 | 18.1933 | YES | 25
31 | 1.47 | 132 | 194.04 | 12 | 6.93 | 17.4379 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2