## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-11-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0.8 | 1 | -0.2 | OK | 0.29
2 | 32 | 1 | 31 | Change Filter | 0.34
3 | 31 | 1 | 30 | Change Filter | 0.21
4 | 31 | 1 | 30 | Change Filter | 0.12
5 | 31 | 1 | 30 | Change Filter | 0.11
6 | 31 | 1 | 30 | Change Filter | 0.16
7 | 30 | 1 | 29 | Change Filter | 0.17
8 | 30 | 1 | 29 | Change Filter | 0.1
9 | 31 | 1 | 30 | Change Filter | 0.09
10 | 33 | 1 | 32 | Change Filter | 0.13
11 | 35 | 1 | 34 | Change Filter | 0.1
12 | 31 | 1 | 30 | Change Filter | 0.14
13 | 28 | 1 | 27 | OK | 0.22
14 | 30 | 1 | 29 | Change Filter | 0.24
15 | 31 | 1 | 30 | Change Filter | 0.1
16 | 32 | 1 | 31 | Change Filter | 0.12
17 | 32 | 1 | 31 | Change Filter | 0.08
18 | 30 | 1 | 29 | Change Filter | 0.24
19 | 29 | 1 | 28 | Change Filter | 0.19
20 | 29 | 1 | 28 | Change Filter | 0.15
21 | 30 | 1 | 29 | Change Filter | 0.19
22 | 28 | 1 | 27 | OK | 0.27
23 | 28 | 1 | 27 | OK | 0.3
24 | 28 | 1 | 27 | OK | 0.15
25 | 30 | 1 | 29 | Change Filter | 0.12
26 | 31 | 1 | 30 | Change Filter | 0.12
27 | 34 | 1 | 33 | Change Filter | 0.18
28 | 34 | 1 | 33 | Change Filter | 0.1
29 | 8 | 1 | 7 | OK | 0.08
30 | 28 | 1 | 27 | OK | 0.12
31 |  |  |  | Change Filter
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-12-03
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-11-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.33 | 132 | 175.56 | 12.4 | 7.03 | 17.3189 | YES | 25
2 | 1.3 | 132 | 171.6 | 11.9 | 6.91 | 17.1086 | YES | 25
3 | 0.78 | 132 | 102.96 | 11.8 | 6.77 | 15.5183 | YES | 25
4 | 0.45 | 132 | 59.4 | 11.1 | 6.84 | 16.0244 | YES | 25
5 | 0.34 | 132 | 44.88 | 11.8 | 6.91 | 15.511 | YES | 25
6 | 0.3 | 132 | 39.6 | 11 | 7 | 16.7489 | YES | 25
7 | 0.29 | 132 | 38.28 | 12.3 | 7 | 15.4078 | YES | 25
8 | 1.56 | 132 | 205.92 | 12.5 | 6.96 | 16.9004 | YES | 25
9 | 1.31 | 132 | 172.92 | 13.2 | 6.84 | 14.9959 | YES | 25
10 | 1.18 | 132 | 155.76 | 12.7 | 6.89 | 15.5624 | YES | 25
11 | 0.83 | 132 | 109.56 | 12.2 | 6.92 | 16.0011 | YES | 25
12 | 0.46 | 132 | 60.72 | 12.1 | 6.94 | 15.5751 | YES | 25
13 | 0.36 | 132 | 47.52 | 12.2 | 6.98 | 15.5181 | YES | 25
14 | 0.35 | 132 | 46.2 | 12 | 6.96 | 15.593 | YES | 25
15 | 1.53 | 132 | 201.96 | 10.9 | 6.71 | 17.472 | YES | 25
16 | 1.3 | 132 | 171.6 | 9.8 | 6.92 | 19.6601 | YES | 25
17 | 1.23 | 132 | 162.36 | 11.6 | 6.74 | 16.3352 | YES | 25
18 | 0.88 | 132 | 116.16 | 11 | 6.8 | 16.6716 | YES | 25
19 | 0.34 | 132 | 44.88 | 11.3 | 6.85 | 15.6884 | YES | 25
20 | 0.83 | 132 | 109.56 | 11.4 | 6.88 | 16.6087 | YES | 25
21 | 0.48 | 132 | 63.36 | 12.2 | 6.9 | 15.3039 | YES | 25
22 | 1.62 | 132 | 213.84 | 12.7 | 6.9 | 16.4224 | YES | 25
23 | 1.54 | 132 | 203.28 | 11.6 | 6.9 | 17.8458 | YES | 25
24 | 1.25 | 132 | 165 | 11.6 | 6.86 | 17.0518 | YES | 25
25 | 1.19 | 132 | 157.08 | 12.1 | 6.91 | 16.6897 | YES | 25
26 | 0.8 | 132 | 105.6 | 11.2 | 6.79 | 16.2628 | YES | 25
27 | 0.63 | 132 | 83.16 | 12.5 | 6.9 | 14.8682 | YES | 25
28 | 0.52 | 132 | 68.64 | 9.2 | 6.99 | 19.2019 | YES | 25
29 | 1.82 | 132 | 240.24 | 10.2 | 6.91 | 20.2289 | YES | 25
30 | 1.45 | 132 | 191.4 | 10.5 | 6.92 | 19.1018 | YES | 25
31 |  | 132 | [5 empty] | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2