## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-12-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | OK |  | 0.14
2 | 11 | 28 | -17 | OK |  | 0.13
3 | 21 | 28 | -7 | OK |  | 0.1
4 | 26 | 29 | -3 | OK |  | 0.13
5 | 13 | 31 | -18 | OK |  | 0.11
6 | 13 | 31 | -18 | OK |  | 0.12
7 | 2 | 29 | -27 | OK |  | 0.96
8 | 42 | 30 | 12 | OK |  | 0.26
9 | 16 | 30 | -14 | OK |  | 0.13
10 | 17 | 30 | -13 | OK |  | 0.11
11 | 21 | 30 | -9 | OK |  | 0.1
12 | 20 | 28 | -8 | OK |  | 0.18
13 | 8 | 31 | -23 | OK |  | 0.18
14 | 11 | 31 | -20 | OK |  | 0.23
15 | 12 | 29 | -17 | OK |  | 0.26
16 | 17 | 29 | -12 | OK |  | 0.16
17 | 18 | 29 | -11 | OK |  | 0.15
18 | 16 | 30 | -14 | OK |  | 0.18
19 | 19 | 31 | -12 | OK |  | 0.26
20 | 25 | 31 | -6 | OK |  | 0.16
21 | 17 | 30 | -13 | OK |  | 0.25
22 | 17 | 25 | -8 | OK |  | 0.14
23 | 18 | 31 | -13 | OK |  | 0.2
24 | 11 | 35 | -24 | OK |  | 0.27
25 | 11 | 29 | -18 | OK |  | 0.15
26 | 20 | 25 | -5 | OK |  | 0.25
27 | 10 | 39 | -29 | OK |  | 0.25
28 | 25 | 30 | -5 | OK |  | 0.26
29 | 8 | 24 | -16 | OK |  | 0.29
30 | 12 | 24 | -12 | OK |  | 0.26
31 | 14 | 24 | -10 | OK |  | 0.27
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2024-01-07
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2024-12-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.63 | 132 | 83.16 | 10.9 | 6.91 | 16.9484 | YES | 25
2 | 0.49 | 132 | 64.68 | 12.1 | 6.93 | 15.5732 | YES | 25
3 | 0.22 | 132 | 29.04 | 11.5 | 6.93 | 15.7091 | YES | 25
4 | 1.9 | 132 | 250.8 | 12 | 6.94 | 18.3469 | YES | 25
5 | 1.87 | 132 | 246.84 | 12.3 | 6.77 | 16.9238 | YES | 25
6 | 1.38 | 132 | 182.16 | 12.6 | 6.9 | 16.0869 | YES | 25
7 | 0.77 | 132 | 101.64 | 13 | 6.48 | 12.4983 | YES | 25
8 | 0.67 | 132 | 88.44 | 11.5 | 6.95 | 16.6077 | YES | 25
9 | 0.55 | 132 | 72.6 | 9.7 | 6.93 | 18.2701 | YES | 25
10 | 0.23 | 132 | 30.36 | 11.8 | 6.88 | 15.1749 | YES | 25
11 | 1.92 | 132 | 253.44 | 12.2 | 6.91 | 17.9657 | YES | 25
12 | 1.6 | 132 | 211.2 | 11.9 | 6.89 | 17.5608 | YES | 25
13 | 1.36 | 132 | 179.52 | 11.8 | 6.93 | 17.451 | YES | 25
14 | 0.63 | 132 | 83.16 | 12.3 | 6.88 | 15.3523 | YES | 25
15 | 0.9 | 132 | 118.8 | 11.9 | 7.09 | 17.4118 | YES | 25
16 | 0.54 | 132 | 71.28 | 11.6 | 7 | 16.5484 | YES | 25
17 | 0.44 | 132 | 58.08 | 12.3 | 7.03 | 15.8182 | YES | 25
18 | 0.26 | 132 | 34.32 | 12.5 | 7.03 | 14.958 | YES | 25
19 | 1.33 | 132 | 175.56 | 12.9 | 6.77 | 14.9413 | YES | 25
20 | 1.55 | 132 | 204.6 | 13.3 | 6.77 | 14.917 | YES | 25
21 | 1.59 | 132 | 209.88 | 12.5 | 6.8 | 15.9834 | YES | 25
22 | 0.75 | 132 | 99 | 12.8 | 6.78 | 14.1305 | YES | 25
23 | 0.82 | 132 | 108.24 | 12.4 | 6.9 | 15.6769 | YES | 25
24 | 1.9 | 132 | 250.8 | 12.7 | 6.99 | 17.5271 | YES | 25
25 | 2 | 132 | 264 | 12.2 | 6.93 | 18.2499 | YES | 25
26 | 1.32 | 132 | 174.24 | 12.2 | 6.86 | 16.5375 | YES | 25
27 | 0.72 | 132 | 95.04 | 12.6 | 6.9 | 14.9216 | YES | 25
28 | 2.1 | 132 | 277.2 | 12.8 | 6.95 | 17.5497 | YES | 25
29 | 0.93 | 132 | 122.76 | 13 | 7.09 | 15.9659 | YES | 25
30 | 1.38 | 132 | 182.16 | 11.6 | 6.95 | 17.8372 | YES | 25
31 | 2.2 | 132 | 290.4 | 10 | 6.9 | 21.3144 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2