## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-01-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 10 | 15 | -5 | OK |  | 0.22
2 | 10 | 15 | -5 | OK |  | 0.23
3 | 10 | 15 | -5 | OK |  | 1.09
4 | 10 | 15 | -5 | OK |  | 0.52
5 | 10 | 15 | -5 | OK |  | 0.3
6 | 11 | 14 | -3 | OK |  | 0.29
7 | 11 | 14 | -3 | OK |  | 0.27
8 | 12 | 13 | -1 | OK |  | 0.26
9 | 12 | 13 | -1 | OK |  | 0.16
10 | 12 | 13 | -1 | OK |  | 0.22
11 | 12 | 13 | -1 | OK |  | 0.19
12 | 13 | 13 | 0 | OK |  | 0.18
13 | 18 | 12 | 6 | OK |  | 0.25
14 | 12 | 13 | -1 | OK |  | 0.2
15 | 14 | 12 | 2 | OK |  | 0.19
16 | 14 | 12 | 2 | OK |  | 0.2
17 | 14 | 12 | 2 | OK |  | 0.29
18 | 14 | 12 | 2 | OK |  | 0.29
19 | 14 | 12 | 2 | OK |  | 0.29
20 | 14 | 12 | 2 | OK |  | 0.25
21 | 14 | 12 | 2 | OK |  | 0.28
22 | 16 | 5 | 11 | OK |  | 0.17
23 | 16 | 5 | 11 | OK |  | 0.24
24 | 16 | 5 | 11 | OK |  | 0.22
25 | 16 | 5 | 11 | OK |  | 0.28
26 | 15 | 5 | 10 | OK |  | 0.19
27 | 16 | 5 | 11 | OK |  | 0.2
28 | 11 | 5 | 6 | OK |  | 0.16
29 | 16 | 5 | 11 | OK |  | 0.24
30 | 17 | 5 | 12 | OK |  | 0.21
31 | 17 | 6 | 11 | OK |  | 0.21
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2025-02-04
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-01-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 132 | 290.4 | 12.5 | 7.01 | 18.5131 | YES | 25
2 | 2.2 | 132 | 290.4 | 12.8 | 6.9 | 17.4253 | YES | 25
3 | 1.11 | 132 | 146.52 | 12.8 | 6.96 | 15.7391 | YES | 25
4 | 2.2 | 132 | 290.4 | 12.5 | 6.94 | 18.041 | YES | 25
5 | 2.08 | 132 | 274.56 | 12.1 | 6.99 | 18.919 | YES | 25
6 | 1.18 | 132 | 155.76 | 12.2 | 6.86 | 16.2873 | YES | 25
7 | 0.93 | 132 | 122.76 | 12.1 | 6.72 | 15.2188 | YES | 25
8 | 0.66 | 132 | 87.12 | 11.2 | 6.65 | 15.2808 | YES | 25
9 | 0.61 | 132 | 80.52 | 12.3 | 6.88 | 15.3193 | YES | 25
10 | 2.11 | 132 | 278.52 | 12.2 | 6.8 | 17.6668 | YES | 25
11 | 1.49 | 132 | 196.68 | 11.1 | 6.88 | 18.2032 | YES | 25
12 | 1.12 | 132 | 147.84 | 9.6 | 6.85 | 19.0546 | YES | 25
13 | 0.9 | 132 | 118.8 | 11.8 | 6.78 | 15.7738 | YES | 25
14 | 0.62 | 132 | 81.84 | 11.9 | 6.83 | 15.4653 | YES | 25
15 | 0.49 | 132 | 64.68 | 12.3 | 6.82 | 14.8228 | YES | 25
16 | 1.8 | 132 | 237.6 | 12.3 | 6.8 | 16.9671 | YES | 25
17 | 1.27 | 132 | 167.64 | 6.97 | 6.92 | 23.6047 | YES | 25
18 | 0.87 | 132 | 114.84 | 11.2 | 6.97 | 17.422 | YES | 25
19 | 0.79 | 132 | 104.28 | 11.6 | 7.05 | 17.2989 | YES | 25
20 | 0.64 | 132 | 84.48 | 11.5 | 7.02 | 16.9519 | YES | 25
21 | 0.55 | 132 | 72.6 | 11.8 | 7.13 | 17.0956 | YES | 25
22 | 0.46 | 132 | 60.72 | 12 | 7.08 | 16.4323 | YES | 25
23 | 1.52 | 132 | 200.64 | 12 | 7.09 | 18.5239 | YES | 25
24 | 1.64 | 132 | 216.48 | 11.9 | 7.09 | 18.8938 | YES | 25
25 | 1.47 | 132 | 194.04 | 12.6 | 6.75 | 15.3743 | YES | 25
26 | 1.25 | 132 | 165 | 10.9 | 6.73 | 17.0597 | YES | 25
27 | 0.69 | 132 | 91.08 | 11.5 | 6.78 | 15.7145 | YES | 25
28 | 0.57 | 132 | 75.24 | 11.6 | 6.8 | 15.5185 | YES | 25
29 | 0.86 | 132 | 113.52 | 11 | 6.73 | 16.2453 | YES | 25
30 | 0.47 | 132 | 62.04 | 11.6 | 6.88 | 15.7704 | YES | 25
31 | 1.89 | 132 | 249.48 | 12.2 | 6.93 | 18.0297 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2