## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-02-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 30 | 1 | 29 | Change Filter |  | 0.22
2 | 39 | 1 | 38 | Change Filter |  | 0.3
3 | 32 | 1 | 31 | Change Filter |  | 0.24
4 | 32 | 1 | 31 | Change Filter |  | 0.5
5 | 28 | 1 | 27 | OK |  | 0.27
6 | 38 | 1 | 37 | Change Filter |  | 0.21
7 | 32 | 1 | 31 | Change Filter |  | 0.29
8 | 32 | 1 | 31 | Change Filter |  | 0.23
9 | 29 | 1 | 28 | Change Filter |  | 0.25
10 | 26 | 1 | 25 | OK |  | 0.15
11 | 50 | 1 | 49 | Change Filter |  | 0.25
12 | 40 | 1 | 39 | Change Filter |  | 0.18
13 | 39 | 1 | 38 | Change Filter |  | 0.19
14 | 30 | 1 | 29 | Change Filter |  | 0.39
15 | 30 | 1 | 29 | Change Filter |  | 0.31
16 | 38 | 1 | 37 | Change Filter |  | 0.37
17 | 38 | 1 | 37 | Change Filter |  | 0.21
18 | 30 | 1 | 29 | Change Filter |  | 0.29
19 | 30 | 1 | 29 | Change Filter |  | 0.21
20 | 31 | 1 | 30 | Change Filter |  | 0.28
21 | 35 | 1 | 34 | Change Filter |  | 0.17
22 | 35 | 1 | 34 | Change Filter |  | 0.28
23 | 35 | 1 | 34 | Change Filter |  | 0.82
24 | 29 | 1 | 28 | Change Filter |  | 0.46
25 | 30 | 1 | 29 | Change Filter |  | 0.26
26 | 30 | 1 | 29 | Change Filter |  | 0.17
27 | 45 | 1 | 44 | Change Filter |  | 0.24
28 | 45 | 1 | 44 | Change Filter |  | 0.23
29
30 | [5 empty] | .
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2025-03-05
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-02-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.1 | 132 | 277.2 | 12.1 | 6.85 | 18.0684 | YES | 25
2 | 0.75 | 132 | 99 | 12.1 | 7.01 | 16.4569 | YES | 25
3 | 0.48 | 132 | 63.36 | 11.4 | 7.06 | 16.9944 | YES | 25
4 | 0.42 | 132 | 55.44 | 10.9 | 7.14 | 17.9161 | YES | 25
5 | 0.55 | 132 | 72.6 | 10.7 | 7.22 | 18.9261 | YES | 25
6 | 1.89 | 132 | 249.48 | 11.4 | 6.77 | 17.9687 | YES | 25
7 | 1.02 | 132 | 134.64 | 11.1 | 6.85 | 17.1095 | YES | 25
8 | 1 | 132 | 132 | 10 | 6.81 | 18.0722 | YES | 25
9 | 0.68 | 132 | 89.76 | 10.6 | 6.82 | 16.847 | YES | 25
10 | 0.78 | 132 | 102.96 | 10.5 | 6.9 | 17.6164 | YES | 25
11 | 0.66 | 132 | 87.12 | 10.8 | 6.81 | 16.5411 | YES | 25
12 | 0.58 | 132 | 76.56 | 10.2 | 6.9 | 17.5684 | YES | 25
13 | 2.1 | 132 | 277.2 | 11.4 | 6.85 | 18.9046 | YES | 25
14 | 2.18 | 132 | 287.76 | 11.3 | 6.93 | 19.7373 | YES | 25
15 | 0.88 | 132 | 116.16 | 11.3 | 6.95 | 17.2118 | YES | 25
16 | 0.58 | 132 | 76.56 | 12.4 | 7.1 | 16.3407 | YES | 25
17 | 0.48 | 132 | 63.36 | 12.2 | 7.14 | 16.5941 | YES | 25
18 | 0.44 | 132 | 58.08 | 12.5 | 7.21 | 16.3206 | YES | 25
19 | 2.14 | 132 | 282.48 | 12 | 7.25 | 20.9842 | YES | 25
20 | 1.52 | 132 | 200.64 | 11.6 | 7.29 | 20.3766 | YES | 25
21 | 0.92 | 132 | 121.44 | 11.8 | 7.34 | 19.1397 | YES | 25
22 | 0.82 | 132 | 108.24 | 12.9 | 7 | 15.3522 | YES | 25
23 | 1.28 | 132 | 168.96 | 13.4 | 6.98 | 15.532 | YES | 25
24 | 0.46 | 132 | 60.72 | 13.6 | 7.08 | 14.4852 | YES | 25
25 | 1.13 | 132 | 149.16 | 12.2 | 7.05 | 17.2791 | YES | 25
26 | 1.66 | 132 | 219.12 | 12 | 7.11 | 18.9439 | YES | 25
27 | 1 | 132 | 132 | 12.3 | 7.13 | 17.3943 | YES | 25
28 | 0.58 | 132 | 76.56 | 12.4 | 6.91 | 15.3275 | YES | 25
29
30
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2