## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-03-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 42 | 1 | 41 | Change Filter |  | 0.19
2 | 39 | 1 | 38 | Change Filter |  | 0.19
3 | 31 | 1 | 30 | Change Filter |  | 0.28
4 | 31 | 1 | 30 | Change Filter |  | 0.29
5 | 31 | 1 | 30 | Change Filter |  | 0.19
6 | 31 | 1 | 30 | Change Filter |  | 0.23
7 | 31 | 1 | 30 | Change Filter |  | 0.29
8 | 40 | 1 | 39 | Change Filter |  | 0.23
9 | 37 | 1 | 36 | Change Filter |  | 0.18
10 | 36 | 1 | 35 | Change Filter |  | 0.18
11 | 37 | 1 | 36 | Change Filter |  | 0.19
12 | 31 | 1 | 30 | Change Filter |  | 0.41
13 | 31 | 1 | 30 | Change Filter |  | 0.67
14 | 34 | 1 | 33 | Change Filter |  | 0.37
15 | 39 | 1 | 38 | Change Filter |  | 0.26
16 | 39 | 1 | 38 | Change Filter |  | 0.67
17 | 36 | 1 | 35 | Change Filter |  | 0.35
18 | 29 | 1 | 28 | Change Filter |  | 0.29
19 | 30 | 1 | 29 | Change Filter |  | 0.3
20 | 35 | 1 | 34 | Change Filter |  | 0.37
21 | 40 | 1 | 39 | Change Filter |  | 0.47
22 | 28 | 1 | 27 | OK |  | 0.43
23 | 40 | 1 | 39 | Change Filter |  | 0.4
24 | 31 | 1 | 30 | Change Filter |  | 0.29
25 | 31 | 1 | 30 | Change Filter |  | 0.26
26 | 28 | 1 | 27 | OK |  | 0.31
27 | 27 | 1 | 26 | OK |  | 0.2
28 | 28 | 1 | 27 | OK |  | 0.44
29 | 23 | 1 | 22 | OK |  | 0.33
30 | 23 | 1 | 22 | OK |  | 0.24
31 | 25 | 1 | 24 | OK |  | 0.37
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2025-04-02
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-03-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.34 | 132 | 44.88 | 12.1 | 7.09 | 16.1712 | YES | 25
2 | 0.33 | 132 | 43.56 | 11 | 6.67 | 15.0348 | YES | 25
3 | 0.51 | 132 | 67.32 | 12 | 6.64 | 14.2563 | YES | 25
4 | 1.23 | 132 | 162.36 | 12 | 6.74 | 15.9261 | YES | 25
5 | 0.73 | 132 | 96.36 | 11.6 | 6.64 | 14.9643 | YES | 25
6 | 0.5 | 132 | 66 | 11.7 | 6.75 | 15.0512 | YES | 25
7 | 0.46 | 132 | 60.72 | 10.9 | 6.88 | 16.4681 | YES | 25
8 | 0.27 | 132 | 35.64 | 10.9 | 6.71 | 15.2347 | YES | 25
9 | 0.99 | 132 | 130.68 | 11 | 6.82 | 16.9883 | YES | 25
10 | 0.3 | 132 | 39.6 | 12 | 6.85 | 14.9482 | YES | 25
11 | 0.47 | 132 | 62.04 | 11.7 | 6.83 | 15.41 | YES | 25
12 | 0.65 | 132 | 85.8 | 11.5 | 6.76 | 15.5419 | YES | 25
13 | 1.4 | 132 | 184.8 | 10.8 | 6.8 | 17.8773 | YES | 25
14 | 1.61 | 132 | 212.52 | 10.6 | 6.73 | 18.0934 | YES | 25
15 | 0.88 | 132 | 116.16 | 11 | 6.93 | 17.4264 | YES | 25
16 | 0.75 | 132 | 99 | 12.1 | 6.95 | 16.1262 | YES | 25
17 | 0.78 | 132 | 102.96 | 11.4 | 6.73 | 15.7023 | YES | 25
18 | 1.74 | 132 | 229.68 | 11.1 | 6.77 | 18.0187 | YES | 25
19 | 0.72 | 132 | 95.04 | 11 | 6.83 | 16.5509 | YES | 25
20 | 0.73 | 132 | 96.36 | 11.4 | 6.83 | 16.1531 | YES | 25
21 | 0.56 | 132 | 73.92 | 10.9 | 6.8 | 16.2034 | YES | 25
22 | 0.61 | 132 | 80.52 | 11.8 | 6.98 | 16.3531 | YES | 25
23 | 0.85 | 132 | 112.2 | 12.2 | 6.8 | 15.4011 | YES | 25
24 | 1.86 | 132 | 245.52 | 12.5 | 6.6 | 15.3056 | YES | 25
25 | 1.68 | 132 | 221.76 | 13 | 6.6 | 14.5022 | YES | 25
26 | 1.48 | 132 | 195.36 | 13.9 | 6.7 | 13.8518 | YES | 25
27 | 2.17 | 132 | 286.44 | 11.8 | 6.7 | 17.6326 | YES | 25
28 | 2.2 | 132 | 290.4 | 11.6 | 6.77 | 18.3561 | YES | 25
29 | 1.26 | 132 | 166.32 | 10.5 | 6.78 | 17.8242 | YES | 25
30 | 0.92 | 132 | 121.44 | 11.1 | 6.88 | 17.0971 | YES | 25
31 | 0.59 | 132 | 77.88 | 10.7 | 6.76 | 16.2428 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2