## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-04-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 25 | 1 | 24 | OK |  | 0.41
2 | 25 | 1 | 24 | OK |  | 0.29
3 | 26 | 1 | 25 | OK |  | 0.25
4 | 26 | 1 | 25 | OK |  | 0.24
5 | 26 | 1 | 25 | OK |  | 0.21
6 | 26 | 1 | 25 | OK |  | 0.25
7 | 28 | 1 | 27 | OK |  | 0.35
8 | 31 | 1 | 30 | Change Filter |  | 0.24
9 | 31 | 1 | 30 | Change Filter |  | 0.31
10 | 31 | 1 | 30 | Change Filter |  | 0.3
11 | 31 | 1 | 30 | Change Filter |  | 0.29
12 | 34 | 1 | 33 | Change Filter |  | 0.32
13 | 40 | 1 | 39 | Change Filter |  | 0.24
14 | 30 | 1 | 29 | Change Filter |  | 0.2
15 | 32 | 1 | 31 | Change Filter |  | 0.19
16 | 30 | 1 | 29 | Change Filter |  | 0.22
17 | 32 | 1 | 31 | Change Filter |  | 0.18
18 | 40 | 1 | 39 | Change Filter |  | 0.17
19 | 40 | 1 | 39 | Change Filter |  | 0.17
20 | 40 | 1 | 39 | Change Filter |  | 0.18
21 | 35 | 1 | 34 | Change Filter |  | 0.21
22 | 29 | 1 | 28 | Change Filter |  | 0.31
23 | 30 | 1 | 29 | Change Filter |  | 0.38
24 | 30 | 1 | 29 | Change Filter |  | 0.25
25 | 30 | 1 | 29 | Change Filter |  | 0.24
26 | 30 | 1 | 29 | Change Filter |  | 0.16
27 | 30 | 1 | 29 | Change Filter |  | 0.19
28 | 30 | 1 | 29 | Change Filter |  | 0.19
29 | 32 | 1 | 31 | Change Filter |  | 0.2
30 | 30 | 1 | 29 | Change Filter |  | 0.29
31 |  |  |  | Change Filter
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2025-05-09
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.56 | 132 | 73.92 | 11.4 | 6.7 | 15.1805 | YES | 25
2 | 0.6 | 132 | 79.2 | 11.7 | 6.82 | 15.5753 | YES | 25
3 | 0.64 | 132 | 84.48 | 10.4 | 6.75 | 16.5896 | YES | 25
4 | 0.75 | 132 | 99 | 11.7 | 6.65 | 14.9526 | YES | 25
5 | 0.39 | 132 | 51.48 | 12.6 | 6.81 | 13.8978 | YES | 25
6 | 1.24 | 132 | 163.68 | 12.2 | 6.9 | 16.6179 | YES | 25
7 | 1.56 | 132 | 205.92 | 12 | 6.7 | 16.2854 | YES | 25
8 | 1.78 | 132 | 234.96 | 11.5 | 6.79 | 17.7597 | YES | 25
9 | 1.72 | 132 | 227.04 | 11.6 | 6.8 | 17.59 | YES | 25
10 | 1.49 | 132 | 196.68 | 12.8 | 6.94 | 16.3136 | YES | 25
11 | 1.13 | 132 | 149.16 | 11.6 | 6.9 | 17.0602 | YES | 25
12 | 0.62 | 132 | 81.84 | 12.5 | 6.92 | 14.9619 | YES | 25
13 | 0.4 | 132 | 52.8 | 12.8 | 6.88 | 14.0905 | YES | 25
14 | 0.58 | 132 | 76.56 | 12.6 | 6.72 | 13.7357 | YES | 25
15 | 0.56 | 132 | 73.92 | 13 | 6.72 | 13.3421 | YES | 25
16 | 0.68 | 132 | 89.76 | 13.1 | 6.86 | 14.1539 | YES | 25
17 | 0.32 | 132 | 42.24 | 12.3 | 6.99 | 15.4059 | YES | 25
18 | 0.24 | 132 | 31.68 | 11.5 | 7.01 | 16.1737 | YES | 25
19 | 2.12 | 132 | 279.84 | 12.5 | 6.95 | 17.944 | YES | 25
20 | 1.8 | 132 | 237.6 | 12.4 | 6.96 | 17.8056 | YES | 25
21 | 1.04 | 132 | 137.28 | 12.5 | 6.66 | 14.2527 | YES | 25
22 | 0.56 | 132 | 73.92 | 12.2 | 6.81 | 14.9782 | YES | 25
23 | 0.6 | 132 | 79.2 | 12.5 | 6.77 | 14.1194 | YES | 25
24 | 0.64 | 132 | 84.48 | 12.9 | 6.77 | 13.8096 | YES | 25
25 | 0.88 | 132 | 116.16 | 12.3 | 6.88 | 15.7724 | YES | 25
26 | 1.04 | 132 | 137.28 | 12.9 | 6.9 | 15.1692 | YES | 25
27 | 0.83 | 132 | 109.56 | 12.5 | 6.86 | 14.9872 | YES | 25
28 | 0.72 | 132 | 95.04 | 12.4 | 6.72 | 14.603 | YES | 25
29 | 0.58 | 132 | 76.56 | 12.4 | 6.72 | 14.3865 | YES | 25
30 | 0.6 | 132 | 79.2 | 13.6 | 6.77 | 13.117 | YES | 25
31 | [7 empty] | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2