## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-05-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 30 | 1 | 29 | Change Filter |  | 0.22
2 | 31 | 1 | 30 | Change Filter |  | 0.24
3 | 32 | 1 | 31 | Change Filter |  | 0.17
4 | 32 | 1 | 31 | Change Filter |  | 0.16
5 | 29 | 1 | 28 | Change Filter |  | 0.2
6 | 29 | 1 | 28 | Change Filter |  | 0.39
7 | 34 | 1 | 33 | Change Filter |  | 0.23
8 | 31 | 1 | 30 | Change Filter |  | 0.21
9 | 28 | 1 | 27 | OK |  | 0.23
10 | 30 | 1 | 29 | Change Filter |  | 0.15
11 | 32 | 1 | 31 | Change Filter |  | 0.2
12 | 26 | 1 | 25 | OK |  | 0.17
13 | 30 | 1 | 29 | Change Filter |  | 0.23
14 | 31 | 1 | 30 | Change Filter |  | 0.23
15 | 31 | 1 | 30 | Change Filter |  | 0.23
16 | 30 | 1 | 29 | Change Filter |  | 0.17
17 | 34 | 1 | 33 | Change Filter |  | 0.12
18 | 34 | 1 | 33 | Change Filter |  | 0.19
19 | 34 | 1 | 33 | Change Filter |  | 0.15
20 | 35 | 1 | 34 | Change Filter |  | 0.13
21 | 31 | 1 | 30 | Change Filter |  | 0.18
22 | 32 | 1 | 31 | Change Filter |  | 0.13
23 | 30 | 1 | 29 | Change Filter |  | 0.19
24 | 34 | 1 | 33 | Change Filter |  | 0.15
25 | 25 | 1 | 24 | OK |  | 0.17
26 | 25 | 1 | 24 | OK |  | 0.11
27 | 25 | 1 | 24 | OK |  | 0.22
28 | 25 | 1 | 24 | OK |  | 0.13
29 | 28 | 1 | 27 | OK |  | 0.13
30 | 27 | 1 | 26 | OK |  | 0.15
31 | 29 | 1 | 28 | Change Filter |  | 0.18
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2025-06-09
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 132 | 79.2 | 12.4 | 6.77 | 14.6587 | YES | 25
2 | 0.66 | 132 | 87.12 | 13.1 | 6.75 | 13.5559 | YES | 25
3 | 0.75 | 132 | 99 | 12.8 | 6.93 | 14.9394 | YES | 25
4 | 0.79 | 132 | 104.28 | 12.2 | 6.87 | 15.6658 | YES | 25
5 | 1.73 | 132 | 228.36 | 12.4 | 6.61 | 15.6897 | YES | 25
6 | 1.43 | 132 | 188.76 | 14.3 | 6.7 | 13.409 | YES | 25
7 | 1.32 | 132 | 174.24 | 12.8 | 6.64 | 14.3167 | YES | 25
8 | 1.4 | 132 | 184.8 | 12.5 | 6.6 | 14.5234 | YES | 25
9 | 0.75 | 132 | 99 | 12.6 | 6.7 | 13.9014 | YES | 25
10 | 0.77 | 132 | 101.64 | 13.2 | 6.86 | 14.2048 | YES | 25
11 | 0.69 | 132 | 91.08 | 12.5 | 6.8 | 14.4251 | YES | 25
12 | 1.92 | 132 | 253.44 | 12.8 | 6.76 | 16.0276 | YES | 25
13 | 1.7 | 132 | 224.4 | 12.8 | 6.72 | 15.4011 | YES | 25
14 | 1.13 | 132 | 149.16 | 13.4 | 6.76 | 14.0718 | YES | 25
15 | 0.69 | 132 | 91.08 | 12.9 | 6.75 | 13.7858 | YES | 25
16 | 0.53 | 132 | 69.96 | 13.2 | 6.76 | 13.3162 | YES | 25
17 | 0.64 | 132 | 84.48 | 13.3 | 6.95 | 14.3747 | YES | 25
18 | 0.65 | 132 | 85.8 | 12.8 | 6.79 | 14.022 | YES | 25
19 | 1.9 | 132 | 250.8 | 13.2 | 6.65 | 14.9482 | YES | 25
20 | 1.39 | 132 | 183.48 | 13.3 | 6.73 | 14.4314 | YES | 25
21 | 1.48 | 132 | 195.36 | 13 | 6.95 | 16.1389 | YES | 25
22 | 1.06 | 132 | 139.92 | 13.8 | 6.64 | 12.9975 | YES | 25
23 | 0.98 | 132 | 129.36 | 12.4 | 6.68 | 14.8163 | YES | 25
24 | 0.98 | 132 | 129.36 | 13.5 | 6.81 | 13.9982 | YES | 25
25 | 0.54 | 132 | 71.28 | 13.4 | 6.71 | 12.9113 | YES | 25
26 | 1.43 | 132 | 188.76 | 14.4 | 6.72 | 13.4189 | YES | 25
27 | 0.95 | 132 | 125.4 | 13.5 | 6.68 | 13.292 | YES | 25
28 | 1.06 | 132 | 139.92 | 13.9 | 6.6 | 12.7197 | YES | 25
29 | 1.01 | 132 | 133.32 | 13.8 | 6.67 | 13.0685 | YES | 25
30 | 0.76 | 132 | 100.32 | 13.8 | 6.68 | 12.7471 | YES | 25
31 | 0.53 | 132 | 69.96 | 13.9 | 6.86 | 13.1878 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2