## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-07-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 35 | 1 | 34 | Change Filter |  | 0.13
2 | 35 | 1 | 34 | Change Filter |  | 0.15
3 | 37 | 1 | 36 | Change Filter |  | 0.15
4 | 38 | 1 | 37 | Change Filter |  | 0.12
5 | 46 | 1 | 45 | Change Filter |  | 0.18
6 | 10 | 1 | 9 | OK |  | 0.17
7 | 46 | 1 | 45 | Change Filter |  | 0.1
8 | 30 | 1 | 29 | Change Filter |  | 0.13
9 | 46 | 1 | 45 | Change Filter |  | 0.14
10 | 55 | 1 | 54 | Change Filter |  | 0.13
11 | 35 | 1 | 34 | Change Filter |  | 0.11
12 | 40 | 1 | 39 | Change Filter |  | 0.15
13 | 42 | 1 | 41 | Change Filter |  | 0.17
14 | 40 | 1 | 39 | Change Filter |  | 0.15
15 | 35 | 1 | 34 | Change Filter |  | 0.13
16 | 29 | 1 | 28 | Change Filter |  | 0.09
17 | 30 | 1 | 29 | Change Filter |  | 0.14
18 | 35 | 1 | 34 | Change Filter |  | 0.17
19 | 30 | 1 | 29 | Change Filter |  | 0.2
20 | 37 | 1 | 36 | Change Filter |  | 0.19
21 | 38 | 1 | 37 | Change Filter |  | 0.23
22 | 35 | 1 | 34 | Change Filter |  | 0.1
23 | 29 | 1 | 28 | Change Filter |  | 0.13
24 | 30 | 1 | 29 | Change Filter |  | 0.15
25 | 32 | 1 | 31 | Change Filter |  | 0.1
26 | 30 | 1 | 29 | Change Filter |  | 0.16
27 | 29 | 1 | 28 | Change Filter |  | 0.13
28 | 35 | 1 | 34 | Change Filter |  | 0.1
29 | 36 | 1 | 35 | Change Filter |  | 0.18
30 | 38 | 1 | 37 | Change Filter |  | 0.13
31 | 30 | 1 | 29 | Change Filter |  | 0.2
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  | 2025-08-06
[5 empty] | PHONE #: (541) 254-1909 |  | CERT# T2D1-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2025-07-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.51 | 132 | 67.32 | 18.6 | 6.65 | 8.8568 | YES | 25
2 | 0.46 | 132 | 60.72 | 18.1 | 6.62 | 9.0074 | YES | 25
3 | 0.98 | 132 | 129.36 | 18.7 | 6.69 | 9.4308 | YES | 25
4 | 1.29 | 132 | 170.28 | 18.4 | 6.84 | 10.5536 | YES | 25
5 | 0.88 | 132 | 116.16 | 18.2 | 6.49 | 8.9435 | YES | 25
6 | 0.63 | 132 | 83.16 | 18.1 | 6.6 | 9.1177 | YES | 25
7 | 0.54 | 132 | 71.28 | 19.9 | 6.7 | 8.2901 | YES | 25
8 | 0.48 | 132 | 63.36 | 19.5 | 6.78 | 8.7198 | YES | 25
9 | 1.95 | 132 | 257.4 | 20.6 | 6.9 | 10.039 | YES | 25
10 | 0.98 | 132 | 129.36 | 21.5 | 6.59 | 7.5028 | YES | 25
11 | 0.7 | 132 | 92.4 | 20.1 | 6.76 | 8.523 | YES | 25
12 | 0.46 | 132 | 60.72 | 24 | 6.73 | 6.2682 | YES | 25
13 | 0.36 | 132 | 47.52 | 22.1 | 6.72 | 7.0355 | YES | 25
14 | 0.48 | 132 | 63.36 | 22.2 | 6.7 | 7.0325 | YES | 25
15 | 1.98 | 132 | 261.36 | 13.5 | 7.1 | 17.466 | YES | 25
16 | 0.68 | 132 | 89.76 | 12.9 | 6.8 | 14.0283 | YES | 25
17 | 0.59 | 132 | 77.88 | 13.2 | 6.8 | 13.6088 | YES | 25
18 | 0.55 | 132 | 72.6 | 12.6 | 6.82 | 14.2068 | YES | 25
19 | 2.15 | 132 | 283.8 | 13.2 | 6.76 | 16.0199 | YES | 25
20 | 1.15 | 132 | 151.8 | 13.2 | 6.9 | 15.0561 | YES | 25
21 | 0.58 | 132 | 76.56 | 13.1 | 6.83 | 13.838 | YES | 25
22 | 0.67 | 132 | 88.44 | 13.2 | 7 | 14.7927 | YES | 25
23 | 0.74 | 132 | 97.68 | 12.9 | 6.9 | 14.659 | YES | 25
24 | 0.86 | 132 | 113.52 | 12.7 | 6.88 | 14.9496 | YES | 25
25 | 0.62 | 132 | 81.84 | 13.7 | 6.88 | 13.6047 | YES | 25
26 | 0.76 | 132 | 100.32 | 13.5 | 6.87 | 13.9585 | YES | 25
27 | 1.34 | 132 | 176.88 | 13.9 | 6.85 | 14.4132 | YES | 25
28 | 0.65 | 132 | 85.8 | 13.2 | 6.62 | 12.8147 | YES | 25
29 | 0.52 | 132 | 68.64 | 13.4 | 6.83 | 13.4702 | YES | 25
30 | 0.75 | 132 | 99 | 13.5 | 6.86 | 13.8908 | YES | 25
31 | 0.64 | 132 | 84.48 | 13.8 | 6.85 | 13.3946 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2