## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41 | 94489 | WTP ID: TP- | B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 25 | 1 | 24 | OK |  | 0.21 | 0.21
2 | 32 | 1 | 31 | Change Filter |  | 0.16 | 0.16
3 | 18 | 1 | 17 | OK |  | 0.11 | 0.11
4 | 25 | 1 | 24 | OK |  | 0.11 | 0.11
5 | 28 | 1 | 27 | OK |  | 0.12 | 0.12
6 | 28 | 1 | 27 | OK |  | 0.24 | 0.24
7 | 22 | 1 | 21 | OK |  | 0.23 | 0.23
8 | 32 | 1 | 31 | Change Filter |  | 0.16 | 0.16
9 | 20 | 1 | 19 | OK |  | 0.17 | 0.17
10 | 35 | 1 | 34 | Change Filter |  | 0.11 | 0.11
11 | 24 | 1 | 23 | OK |  | 0.22 | 0.22
12 | 28 | 1 | 27 | OK |  | 0.15 | 0.15
13 | 36 | 1 | 35 | Change Filter |  | 0.16 | 0.16
14 | 35 | 1 | 34 | Change Filter |  | 0.2 | 0.2
15 | 28 | 1 | 27 | OK |  | 0.12 | 0.12
16 | 35 | 1 | 34 | Change Filter |  | 0.15 | 0.15
17 | 18 | 1 | 17 | OK |  | 0.18 | 0.18
18 | 30 | 1 | 29 | Change Filter |  | 0.17 | 0.17
19 | 38 | 1 | 37 | Change Filter |  | 0.13 | 0.13
20 | 26 | 1 | 25 | OK |  | 0.16 | 0.16
21 | 33 | 1 | 32 | Change Filter |  | 0.3 | 0.3
22 | 36 | 1 | 35 | Change Filter |  | 0.16 | 0.16
23 | 22 | 1 | 21 | OK |  | 0.2 | 0.2
24 | 35 | 1 | 34 | Change Filter |  | 0.18 | 0.18
25 | 27 | 1 | 26 | OK |  | 0.14 | 0.14
26 | 35 | 1 | 34 | Change Filter |  | 0.17 | 0.17
27 | 38 | 1 | 37 | Change Filter |  | 0.2 | 0.2
28 | 28 | 1 | 27 | OK |  | 0.18 | 0.18
29 | 33 | 1 | 32 | Change Filter |  | 0.22 | 0.22
30 | 35 | 1 | 34 | Change Filter |  | 0.19 | 0.19
31 | 22 | 1 | 21 | OK |  | 0.25 | 0.25
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Giovanni Rangel
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 9/10/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 373-9150 |  | CERT #:T1D1-859079
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  | ID#: 41 | 94489 | Month/Year: | 2025-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.1 | 132 | 145.2 | 14 | 6.64 | 25.7665 | YES | 25
2 | 0.97 | 132 | 128.04 | 13.5 | 6.5 | 24.9173 | YES | 25
3 | 0.71 | 132 | 93.72 | 14 | 6.55 | 23.8265 | YES | 25
4 | 1.12 | 132 | 147.84 | 12.8 | 6.5 | 26.5673 | YES | 25
5 | 0.79 | 132 | 104.28 | 14 | 6.66 | 25.0535 | YES | 25
6 | 0.55 | 132 | 72.6 | 13.6 | 6.75 | 25.8907 | YES | 25
7 | 1.84 | 132 | 242.88 | 14.6 | 6.84 | 29.0164 | YES | 25
8 | 1.46 | 132 | 192.72 | 15.1 | 6.85 | 26.9698 | YES | 25
9 | 0.86 | 132 | 113.52 | 14.8 | 6.88 | 25.98 | YES | 25
10 | 0.97 | 132 | 128.04 | 14.6 | 6.82 | 26.0753 | YES | 25
11 | 0.49 | 132 | 64.68 | 13.4 | 6.97 | 28.2822 | YES | 25
12 | 0.58 | 132 | 76.56 | 12.5 | 6.66 | 27.0457 | YES | 25
13 | 0.65 | 132 | 85.8 | 14.9 | 6.85 | 24.9129 | YES | 25
14 | 0.74 | 132 | 97.68 | 14.3 | 6.86 | 26.3025 | YES | 25
15 | 1.86 | 132 | 245.52 | 15 | 7.2 | 32.3583 | YES | 25
16 | 0.72 | 132 | 95.04 | 14.7 | 6.9 | 25.9313 | YES | 25
17 | 0.55 | 132 | 72.6 | 14.8 | 6.74 | 23.7977 | YES | 25
18 | 0.52 | 132 | 68.64 | 13.7 | 6.78 | 25.9174 | YES | 25
19 | 0.76 | 132 | 100.32 | 13.4 | 6.95 | 28.9517 | YES | 25
20 | 0.68 | 132 | 89.76 | 13.7 | 6.98 | 28.4339 | YES | 25
21 | 0.74 | 132 | 97.68 | 14.2 | 6.32 | 21.6448 | YES | 25
22 | 1.95 | 132 | 257.4 | 13.9 | 6.54 | 27.5447 | YES | 25
23 | 1.29 | 132 | 170.28 | 13.3 | 6.7 | 28.2191 | YES | 25
24 | 0.72 | 132 | 95.04 | 13.8 | 6.79 | 26.4387 | YES | 25
25 | 0.55 | 132 | 72.6 | 13.4 | 6.83 | 27.0329 | YES | 25
26 | 0.5 | 132 | 66 | 15.4 | 6.84 | 23.5906 | YES | 25
27 | 0.52 | 132 | 68.64 | 13.6 | 6.83 | 26.5819 | YES | 25
28 | 0.68 | 132 | 89.76 | 13.7 | 6.91 | 27.704 | YES | 25
29 | 1.96 | 132 | 258.72 | 13.9 | 6.99 | 32.5843 | YES | 25
30 | 1.13 | 132 | 149.16 | 13.5 | 6.68 | 27.137 | YES | 25
31 | 0.65 | 132 | 85.8 | 13.6 | 6.84 | 27.0806 | YES | 25
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2