## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-02-01
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 |  | WTP ID: B-Upper Park
Day | PSI Before Filter | PSI After Filter | PSID | Change Filter ALERT (max is 30 psid) | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 12 | 1 | 11 | OK | 0.15 | 0.15
2 | 12 | 1 | 11 | OK | 0.23 | 0.23
3 | 12 | 1 | 11 | OK | 0.18 | 0.18
4 | 15 | 1 | 14 | OK | 0.16 | 0.16
5 | 16 | 1 | 15 | OK | 0.14 | 0.14
6 | 16 | 1 | 15 | OK | 0.15 | 0.15
7 | 25 | 1 | 24 | OK | 0.16 | 0.16
8 | 26 | 1 | 25 | OK | 0.28 | 0.28
9 | 19 | 1 | 18 | OK | 0.29 | 0.29
10 | 25 | 1 | 24 | OK | 0.21 | 0.21
11 | 26 | 1 | 25 | OK | 0.18 | 0.18
12 | 26 | 1 | 25 | OK | 0.22 | 0.22
13 | 27 | 1 | 26 | OK | 0.16 | 0.16
14 | 27 | 1 | 26 | OK | 0.16 | 0.16
15 | 26 | 1 | 25 | OK | 0.14 | 0.14
16 | 26 | 1 | 25 | OK | 0.22 | 0.22
17 | 27 | 1 | 26 | OK | 0.21 | 0.21
18 | 26 | 1 | 25 | OK | 0.22 | 0.22
19 | 26 | 1 | 25 | OK | 0.19 | 0.19
20 | 26 | 1 | 25 | OK | 0.2 | 0.2
21 | 26 | 1 | 25 | OK | 0.16 | 0.16
22 | 26 | 1 | 25 | OK | 0.17 | 0.17
23 | 27 | 1 | 26 | OK | 0.29 | 0.29
24 | 27 | 1 | 26 | OK | 0.29 | 0.29
25 | 22 | 1 | 21 | OK | 0.26 | 0.26
26 | 22 | 1 | 21 | OK | 0.28 | 0.28
27 | 22 | 1 | 21 | OK | 0.23 | 0.23
28 | 22 | 1 | 21 | OK | 0.26 | 0.26
29 |  |  |  | Change Filter
30 |  |  |  | Change Filter
31 |  |  |  | Change Filter
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Comments: |  |  |  |  | PRINTED NAME: Giovanni Rangel
SIGNATURE: Giovanni Rangel
[5 empty] | PHONE #: (541) 373-9150 |  | CERT# T1D1 - 859079
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum. This form Modified 3/6/2022
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP: B-Upper Park
System Name: | Whaleshead Beach Resort LLC |  |  | ID#: 41-94489 | Month/Year: | 2026-02-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
Daily @ 09:00 | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.99 | 37 | 36.63 | 13.1 | 6.96 | 15.2177 | YES | 20
2 | 0.77 | 37 | 28.49 | 10.8 | 6.98 | 17.7404 | YES | 20
3 | 1.02 | 37 | 37.74 | 12 | 7.01 | 17.0578 | YES | 20
4 | 0.94 | 37 | 34.78 | 13 | 6.95 | 15.1762 | YES | 20
5 | 1.12 | 37 | 41.44 | 12.9 | 6.98 | 15.7686 | YES | 20
6 | 0.75 | 37 | 27.75 | 14 | 6.96 | 13.9424 | YES | 20
7 | 0.81 | 37 | 29.97 | 12.7 | 6.98 | 15.426 | YES | 20
8 | 1 | 37 | 37 | 12.3 | 6.9 | 16.087 | YES | 20
9 | 0.7 | 37 | 25.9 | 10.3 | 7.01 | 18.3685 | YES | 20
10 | 1.6 | 37 | 59.2 | 11.3 | 6.92 | 18.4416 | YES | 20
11 | 0.96 | 37 | 35.52 | 11.7 | 6.95 | 16.9248 | YES | 20
12 | 1.44 | 37 | 53.28 | 12 | 6.88 | 17.0866 | YES | 20
13 | 1.32 | 37 | 48.84 | 11 | 6.82 | 17.6145 | YES | 20
14 | 1.03 | 37 | 38.11 | 11.8 | 6.88 | 16.548 | YES | 20
15 | 1.03 | 37 | 38.11 | 12 | 6.84 | 16.1193 | YES | 20
16 | 0.78 | 37 | 28.86 | 10.8 | 7.03 | 18.0671 | YES | 20
17 | 1.59 | 37 | 58.83 | 9.6 | 6.97 | 20.9377 | YES | 20
18 | 0.8 | 37 | 29.6 | 6.1 | 7.05 | 24.827 | YES | 20
19 | 1.34 | 37 | 49.58 | 8.8 | 6.99 | 21.6066 | YES | 20
20 | 0.88 | 37 | 32.56 | 9.4 | 7.03 | 20.0054 | YES | 20
21 | 1.61 | 37 | 59.57 | 10.7 | 7.02 | 19.871 | YES | 20
22 | 1.31 | 37 | 48.47 | 12 | 7.06 | 17.9135 | YES | 20
23 | 0.88 | 37 | 32.56 | 13.1 | 6.88 | 14.5887 | YES | 20
24 | 0.83 | 37 | 30.71 | 13.6 | 6.85 | 13.8733 | YES | 20
25 | 0.82 | 37 | 30.34 | 12.7 | 6.72 | 14.0234 | YES | 20
26 | 0.88 | 37 | 32.56 | 11.7 | 6.72 | 15.523 | YES | 20
27 | 0.57 | 37 | 21.09 | 11.7 | 6.73 | 15.0637 | YES | 20
28 | 1.49 | 37 | 55.13 | 13.1 | 6.78 | 15.0703 | YES | 20
29 |  | 37 | [5 empty] | 20
30 |  | 37 | [5 empty] | 20
31 |  | 37 | [5 empty] | 20
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised 3/6/2022 PAX
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2