## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-04-21
System Name: | Coos Co Parks-LaVerne |  |  | ID#: 41 | 94557 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.03
2 |  |  | 0.03
3 |  |  | 0.03
4 |  |  | 0.03
5 |  |  | 0.03
6 |  |  | 0.03
7 |  |  | 0.03
8 |  |  | 0.03
9 |  |  | 0.03
10 |  |  | 0.03
11 |  |  | 0.03
12 |  |  | 0.03
13 |  |  | 0.03
14 |  |  | 0.03
15 |  |  | 0.03
16 |  |  | 0.03
17 |  |  | 0.03
18 |  |  | 0.03
19 |  |  | 0.03
20 |  |  | 0.03
21 |  |  | 0.03
22 |  |  | 0.03
23 |  |  | 0.03
24 |  |  | 0.03
25 |  |  | 0.03
26 |  |  | 0.03
27 |  |  | 0.03
28 |  |  | 0.03
29 |  |  | 0.03
30 |  |  | 0.03
31 |  |  | 0.03
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes:
[5 empty] | SIGNATURE: |  |  | 21-4
[5 empty] | PHONE #: ( 541 )396-2344 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : B
System Name: | Coos Co. Parks Lav. |  | ID#: 41 | 94557 | Month/Year: | 2021-04-21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 1.2 | 31.8 | 38.16 | 12 | 7.7 | 22.1017 | YES | 1
2 | 1.2 | 31.8 | 38.16 | 10.8 | 7.8 | 24.7964 | YES | 1
3 | 1.2 | 31.8 | 38.16 | 10.6 | 7.9 | 26.0427 | YES | 1
4 | 1.2 | 31.8 | 38.16 | 9.8 | 7.9 | 27.4814 | YES | 1
5 | 1.2 | 31.8 | 38.16 | 9.6 | 7.8 | 26.8725 | YES | 1
6 | 1.2 | 31.8 | 38.16 | 9.9 | 7.8 | 26.3363 | YES | 1
7 | 1.2 | 31.8 | 38.16 | 11.4 | 8 | 25.5807 | YES | 1
8 | 1.2 | 31.8 | 38.16 | 11.6 | 7.9 | 24.3585 | YES | 1
9 | 1.4 | 31.8 | 44.52 | 10.1 | 8 | 28.5693 | YES | 1
10 | 1.3 | 31.8 | 41.34 | 9 | 8 | 30.4248 | YES | 1
11 | 1.2 | 31.8 | 38.16 | 9.8 | 8.18 | 30.3999 | YES | 1
12 | 1.2 | 31.8 | 38.16 | 9.4 | 8 | 29.2687 | YES | 1
13 | 1.2 | 31.8 | 38.16 | 9.1 | 8 | 29.8699 | YES | 1
14 | 1.2 | 31.8 | 38.16 | 9.9 | 8 | 28.2957 | YES | 1
15 | 1.2 | 31.8 | 38.16 | 10.9 | 8 | 26.4528 | YES | 1
16 | 1.2 | 31.8 | 38.16 | 12.3 | 8.1 | 24.9603 | YES | 1
17 | 1.2 | 31.8 | 38.16 | 12.2 | 7.1 | 17.7127 | YES | 1
18 | 1.2 | 31.8 | 38.16 | 12.3 | 7 | 17.0087 | YES | 1
19 | 1.2 | 31.8 | 38.16 | 14.4 | 6.9 | 13.9753 | YES | 1
20 | 1.2 | 31.8 | 38.16 | 14.8 | 7.1 | 14.6554 | YES | 1
21 | 1.2 | 31.8 | 38.16 | 19.9 | 7.1 | 10.4052 | YES | 1
22 | 1.2 | 31.8 | 38.16 | 15.7 | 6.9 | 12.8098 | YES | 1
23 | 1.2 | 31.8 | 38.16 | 19.9 | 7.1 | 10.4052 | YES | 1
24 | 1.2 | 31.8 | 38.16 | 19 | 7.2 | 11.4781 | YES | 1
25 | 1.2 | 31.8 | 38.16 | 12.3 | 7.4 | 19.5155 | YES | 1
26 | 1.2 | 31.8 | 38.16 | 11.9 | 7.5 | 20.7415 | YES | 1
27 | 1.2 | 31.8 | 38.16 | 13.2 | 7.1 | 16.3064 | YES | 1
28 | 1.2 | 31.8 | 38.16 | 13.8 | 7.2 | 16.258 | YES | 1
29 | 1.3 | 31.8 | 41.34 | 14.7 | 7.1 | 14.9229 | YES | 1
30 | 1.2 | 31.8 | 38.16 | 13 | 7.1 | 16.5251 | YES | 1
31 | 1.2 | 31.8 | 38.16 | 13.8 | 7.1 | 15.6671 | YES | 1
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
yes
yes
yes
yes
Calvin Napier