## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-07-21
System Name: | Coos Co Parks-LaVerne |  |  | ID#: 41 | 94557 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.03
2 |  |  | 0.03
3 |  |  | 0.03
4 |  |  | 0.03
5 |  |  | 0.03
6 |  |  | 0.03
7 |  |  | 0.03
8 |  |  | 0.02
9 |  |  | 0.02
10 |  |  | 0.02
11 |  |  | 0.02
12 |  |  | 0.02
13 |  |  | 0.02
14 |  |  | 0.02
15 |  |  | 0.02
16 |  |  | 0.02
17 |  |  | 0.02
18 |  |  | 0.02
19 |  |  | 0.02
20 |  |  | 0.03
21 |  |  | 0.03
22 |  |  | 0.03
23 |  |  | 0.03
24 |  |  | 0.03
25 |  |  | 0.03
26 |  |  | 0.02
27 |  |  | 0.03
28 |  |  | 0.03
29 |  |  | 0.03
30 |  |  | 0.03
31 |  |  | 0.03
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes:
[5 empty] | SIGNATURE: |  |  | 2021-07-21
[5 empty] | PHONE #: ( 541 )396-2344 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : B
System Name: | Coos Co. Parks Lav. |  | ID#: 41 | 94557 | Month/Year: | 2021-07-21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 1.4 | 31.8 | 44.52 | 22.9 | 6.9 | 8.0555 | YES | 1
2 | 1.4 | 31.8 | 44.52 | 23.1 | 7.1 | 8.5717 | YES | 1
3 | 1.4 | 31.8 | 44.52 | 22 | 7.3 | 9.9594 | YES | 1
4 | 1.4 | 31.8 | 44.52 | 22.2 | 7.1 | 9.1127 | YES | 1
5 | 1.4 | 31.8 | 44.52 | 22.1 | 7.3 | 9.8922 | YES | 1
6 | 1.4 | 31.8 | 44.52 | 23 | 7.6 | 10.4182 | YES | 1
7 | 1.4 | 31.8 | 44.52 | 22.2 | 6.9 | 8.4495 | YES | 1
8 | 1.4 | 31.8 | 44.52 | 22.2 | 7.2 | 9.4626 | YES | 1
9 | 1.4 | 31.8 | 44.52 | 20.6 | 7.2 | 10.5445 | YES | 1
10 | 1.4 | 31.8 | 44.52 | 22.2 | 7.1 | 9.1127 | YES | 1
11 | 1 | 31.8 | 31.8 | 21 | 7 | 9.0889 | YES | 1
12 | 1 | 31.8 | 31.8 | 21.4 | 7.9 | 12.3974 | YES | 1
13 | 1 | 31.8 | 31.8 | 22.9 | 7 | 7.9855 | YES | 1
14 | 1 | 31.8 | 31.8 | 22 | 7 | 8.4912 | YES | 1
15 | 1 | 31.8 | 31.8 | 21.7 | 7.1 | 9 | YES | 1
16 | 1.2 | 31.8 | 38.16 | 23.3 | 7 | 7.9537 | YES | 1
17 | 1.2 | 31.8 | 38.16 | 20.7 | 7.1 | 9.8573 | YES | 1
18 | 1.2 | 31.8 | 38.16 | 20.7 | 7.1 | 9.8573 | YES | 1
19 | 1.2 | 31.8 | 38.16 | 21 | 7 | 9.3021 | YES | 1
20 | 1.2 | 31.8 | 38.16 | 20.3 | 6.8 | 9.0462 | YES | 1
21 | 1.2 | 31.8 | 38.16 | 20.9 | 7.1 | 9.7247 | YES | 1
22 | 1.2 | 31.8 | 38.16 | 20.4 | 7 | 9.6883 | YES | 1
23 | 1 | 31.8 | 31.8 | 20.1 | 6.9 | 9.304 | YES | 1
24 | 1 | 31.8 | 31.8 | 20.5 | 6.9 | 9.0548 | YES | 1
25 | 1 | 31.8 | 31.8 | 20.5 | 7.4 | 10.9267 | YES | 1
26 | 1.2 | 31.8 | 38.16 | 22.8 | 7.3 | 9.218 | YES | 1
27 | 1.2 | 31.8 | 38.16 | 24 | 7.4 | 8.823 | YES | 1
28 | 1.2 | 31.8 | 38.16 | 24.1 | 7 | 7.53 | YES | 1
29 | 1.2 | 31.8 | 38.16 | 24.1 | 7.1 | 7.8218 | YES | 1
30 | 1.2 | 31.8 | 38.16 | 24 | 7.3 | 8.4957 | YES | 1
31 | 1.4 | 31.8 | 44.52 | 23.4 | 7.3 | 9.0576 | YES | 1
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
yes
yes
yes
yes
Calvin Napier