## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-07-22
System Name: | Coos Co Parks-LaVerne |  |  | ID#: 41 | 94557 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.03
2 |  |  | 0.03
3 |  |  | 0.04
4 |  |  | 0.03
5 |  |  | 0.03
6 |  |  | 0.03
7 |  |  | 0.03
8 |  |  | 0.03
9 |  |  | 0.03
10 |  |  | 0.03
11 |  |  | 0.03
12 |  |  | 0.03
13 |  |  | 0.03
14 |  |  | 0.03
15 |  |  | 0.03
16 |  |  | 0.02
17 |  |  | 0.02
18 |  |  | 0.03
19 |  |  | 0.08
20 |  |  | 0.09
21 |  |  | 0.09
22 |  |  | 0.05
23 |  |  | 0.06
24 |  |  | 0.08
25 |  |  | 0.08
26 |  |  | 0.09
27 |  |  | 0.06
28 |  |  | 0.06
29 |  |  | 0.07
30 |  |  | 0.07
31 |  |  | 0.07
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes:
[5 empty] | SIGNATURE: |  |  | 2022-07-22
[5 empty] | PHONE #: ( 541 )396-2344 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : B
System Name: | Coos Co. Parks Lav. |  | ID#: 41 | 94557 | Month/Year: | 2022-07-22 | Disinfection Giardia Log Inactiv: | 0.5 | ``````````````````
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow |  | ``````````````````````````````````````````````````````` | `````````````````````````````````````````````````````````````````````````````````````````````````````````
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 1.4 | 31.8 | 44.52 | 20.5 | 7.4 | 11.4413 | YES | 1
2 | 1.4 | 31.8 | 44.52 | 20 | 7.5 | 12.2827 | YES | 1
3 | 1.2 | 31.8 | 38.16 | 18.6 | 7.45 | 12.9433 | YES | 1
4 | 1.2 | 31.8 | 38.16 | 18.4 | 7.32 | 12.4979 | YES | 1
5 | 1.2 | 31.8 | 38.16 | 20.1 | 7.51 | 11.9682 | YES | 1
6 | 1 | 31.8 | 31.8 | 19.8 | 7.41 | 11.4972 | YES | 1
7 | 1 | 31.8 | 31.8 | 10.2 | 7.4 | 21.897 | YES | 1
8 | 1 | 31.8 | 31.8 | 19.9 | 7.52 | 11.8992 | YES | 1
9 | 0.8 | 31.8 | 25.44 | 18.9 | 7.5 | 12.345 | YES | 1
10 | 1 | 31.8 | 31.8 | 19.1 | 7.6 | 12.936 | YES | 1
11 | 0.8 | 31.8 | 25.44 | 20.4 | 7.51 | 11.2021 | YES | 1
12 | 0.8 | 31.8 | 25.44 | 21.5 | 7.42 | 10.0554 | YES | 1
13 | 0.8 | 31.8 | 25.44 | 22.5 | 7.62 | 10.131 | YES | 1
14 | 0.8 | 31.8 | 25.44 | 21.4 | 7.42 | 10.1236 | YES | 1
15 | 0.8 | 31.8 | 25.44 | 19.8 | 7.4 | 11.1939 | YES | 1
16 | 0.8 | 31.8 | 25.44 | 19.1 | 7.4 | 11.7339 | YES | 1
17 | 0.8 | 31.8 | 25.44 | 19.7 | 7.32 | 10.9371 | YES | 1
18 | 0.8 | 31.8 | 25.44 | 19.9 | 7.4 | 11.1187 | YES | 1
19 | 0.8 | 31.8 | 25.44 | 20 | 7.4 | 11.044 | YES | 1
20 | 1 | 31.8 | 31.8 | 21.3 | 7.21 | 9.639 | YES | 1
21 | 1 | 31.8 | 31.8 | 21.2 | 7.12 | 9.3812 | YES | 1
22 | 1 | 31.8 | 31.8 | 21.2 | 7.13 | 9.4166 | YES | 1
23 | 1 | 31.8 | 31.8 | 21.7 | 7.14 | 9.1369 | YES | 1
24 | 1 | 31.8 | 31.8 | 22.3 | 7.3 | 9.3176 | YES | 1
25 | 0.8 | 31.8 | 25.44 | 22.9 | 7.61 | 9.8235 | YES | 1
26 | 0.8 | 31.8 | 25.44 | 21.8 | 7.56 | 10.3853 | YES | 1
27 | 0.8 | 31.8 | 25.44 | 22.6 | 7.21 | 8.6222 | YES | 1
28 | 0.8 | 31.8 | 25.44 | 19.9 | 7 | 9.5688 | YES | 1
29 | 0.8 | 31.8 | 25.44 | 22 | 7.32 | 9.3617 | YES | 1
30 | 1 | 31.8 | 31.8 | 20.2 | 7.21 | 10.3837 | YES | 1
31 | 0.8 | 31.8 | 25.44 | 23.1 | 7.73 | 10.1385 | YES | 1
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
yes
yes
yes
yes
Calvin Napier