## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-10-22
System Name: | Coos Co Parks-LaVerne |  |  | ID#: 41 | 94557 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.02
2 |  |  | 0.03
3 |  |  | 0.04
4 |  |  | 0.03
5 |  |  | 0.04
6 |  |  | 0.07
7 |  |  | 0.05
8 |  |  | 0.04
9 |  |  | 0.03
10 |  |  | 0.03
11 |  |  | 0.04
12 |  |  | 0.04
13 |  |  | 0.04
14 |  |  | 0.04
15 |  |  | 0.04
16 |  |  | 0.03
17 |  |  | 0.04
18 |  |  | 0.03
19 |  |  | 0.04
20 |  |  | 0.04
21 |  |  | 0.04
22 |  |  | 0.04
23 |  |  | 0.03
24 |  |  | 0.03
25 |  |  | 0.04
26 |  |  | 0.04
27 |  |  | 0.04
28 |  |  | 0.04
29 |  |  | 0.04
30 |  |  | 0.03
31 |  |  | 0.04
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes:
[5 empty] | SIGNATURE: |  |  | 2022-10-22
[5 empty] | PHONE #: ( 541 )396-2344 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : B
System Name: | Coos Co. Parks Lav. |  | ID#: 41 | 94557 | Month/Year: | 2022-10-22 | Disinfection Giardia Log Inactiv: | 0.5 | ``````````````````
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow |  | ``````````````````````````````````````````````````````` | `````````````````````````````````````````````````````````````````````````````````````````````````````````
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 1 | 31.8 | 31.8 | 19.6 | 7.65 | 12.7446 | YES | 1
2 | 0.6 | 31.8 | 19.08 | 19.8 | 7.69 | 12.1915 | YES | 1
3 | 0.6 | 31.8 | 19.08 | 18.8 | 7.46 | 11.9664 | YES | 1
4 | 0.6 | 31.8 | 19.08 | 19.1 | 7.5 | 11.9039 | YES | 1
5 | 0.6 | 31.8 | 19.08 | 19.2 | 7.5 | 11.8241 | YES | 1
6 | 0.6 | 31.8 | 19.08 | 19.3 | 8 | 14.1489 | YES | 1
7 | 0.6 | 31.8 | 19.08 | 19.2 | 8 | 14.2439 | YES | 1
8 | 0.6 | 31.8 | 19.08 | 18.8 | 7.5 | 12.1463 | YES | 1
9 | 0.8 | 31.8 | 25.44 | 18.5 | 7.5 | 12.6809 | YES | 1
10 | 0.6 | 31.8 | 19.08 | 18.6 | 7.6 | 12.7782 | YES | 1
11 | 0.6 | 31.8 | 19.08 | 18.5 | 7.4 | 11.9397 | YES | 1
12 | 0.6 | 31.8 | 19.08 | 17.9 | 7.3 | 11.9755 | YES | 1
13 | 0.6 | 31.8 | 19.08 | 18 | 7.5 | 12.8164 | YES | 1
14 | 0.6 | 31.8 | 19.08 | 18.2 | 7.4 | 12.1828 | YES | 1
15 | 0.6 | 31.8 | 19.08 | 18 | 7.5 | 12.8164 | YES | 1
16 | 0.6 | 31.8 | 19.08 | 17.7 | 7.5 | 13.0769 | YES | 1
17 | 0.6 | 31.8 | 19.08 | 18.1 | 7.4 | 12.2649 | YES | 1
18 | 0.6 | 31.8 | 19.08 | 17.3 | 7.4 | 12.9413 | YES | 1
19 | 0.8 | 31.8 | 25.44 | 16.1 | 7.5 | 14.8907 | YES | 1
20 | 0.8 | 31.8 | 25.44 | 16.2 | 7.4 | 14.2527 | YES | 1
21 | 0.6 | 31.8 | 19.08 | 16.7 | 7.5 | 13.9825 | YES | 1
22 | 0.6 | 31.8 | 19.08 | 16.1 | 7.4 | 14.0243 | YES | 1
23 | 0.6 | 31.8 | 19.08 | 15.9 | 7.4 | 14.2131 | YES | 1
24 | 0.6 | 31.8 | 19.08 | 15.3 | 7.3 | 14.2556 | YES | 1
25 | 0.6 | 31.8 | 19.08 | 15.1 | 7.4 | 14.9936 | YES | 1
26 | 0.6 | 31.8 | 19.08 | 14.8 | 7.4 | 15.2968 | YES | 1
27 | 0.6 | 31.8 | 19.08 | 13.2 | 7.5 | 17.6587 | YES | 1
28 | 0.6 | 31.8 | 19.08 | 13.3 | 7.3 | 16.2913 | YES | 1
29 | 0.6 | 31.8 | 19.08 | 13.5 | 7.4 | 16.6816 | YES | 1
30 | 0.6 | 31.8 | 19.08 | 13.6 | 7.4 | 16.5709 | YES | 1
31 | 0.6 | 31.8 | 19.08 | 13.9 | 7.5 | 16.8551 | YES | 1
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
yes
yes
yes
yes
Calvin Napier