## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-01-22
System Name: | Coos Co Parks-LaVerne |  |  | ID#: 41 | 94557 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.05
2 |  |  | 0.04
3 |  |  | 0.05
4 |  |  | 0.04
5 |  |  | 0.05
6 |  |  | 0.04
7 |  |  | 0.04
8 |  |  | 0.04
9 |  |  | 0.04
10 |  |  | 0.03
11 |  |  | 0.03
12 |  |  | 0.03
13 |  |  | 0.04
14 |  |  | 0.04
15 |  |  | 0.03
16 |  |  | 0.03
17 |  |  | 0.04
18 |  |  | 0.04
19 |  |  | 0.05
20 |  |  | 0.05
21 |  |  | 0.04
22 |  |  | 0.03
23 |  |  | 0.03
24 |  |  | 0.03
25 |  |  | 0.03
26 |  |  | 0.03
27 |  |  | 0.04
28 |  |  | 0.03
29 |  |  | 0.04
30 |  |  | 0.04
31 |  |  | 0.04
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes:
[5 empty] | SIGNATURE: |  |  | 2023-01-22
[5 empty] | PHONE #: ( 541 )396-2344 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : B
System Name: | Coos Co. Parks Lav. |  | ID#: 41 | 94557 | Month/Year: | 2023-01-22 | Disinfection Giardia Log Inactiv: | 0.5 | ``````````````````
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow |  | ``````````````````````````````````````````````````````` | `````````````````````````````````````````````````````````````````````````````````````````````````````````
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 0.8 | 31.8 | 25.44 | 8.7 | 6.5 | 17.2837 | YES | 1
2 | 0.8 | 31.8 | 25.44 | 8.9 | 6.6 | 17.6567 | YES | 1
3 | 0.8 | 31.8 | 25.44 | 9.1 | 6.5 | 16.8473 | YES | 1
4 | 0.8 | 31.8 | 25.44 | 8.7 | 6.6 | 17.8852 | YES | 1
5 | 1 | 31.8 | 31.8 | 8.9 | 6.7 | 18.682 | YES | 1
6 | 1 | 31.8 | 31.8 | 8.7 | 6.5 | 17.6676 | YES | 1
7 | 1 | 31.8 | 31.8 | 8.5 | 6.7 | 19.1727 | YES | 1
8 | 1 | 31.8 | 31.8 | 9 | 6.7 | 18.5615 | YES | 1
9 | 1.2 | 31.8 | 38.16 | 9.6 | 6.5 | 17.0475 | YES | 1
10 | 1.2 | 31.8 | 38.16 | 9.3 | 6.5 | 17.378 | YES | 1
11 | 1.2 | 31.8 | 38.16 | 9.1 | 6.6 | 18.2166 | YES | 1
12 | 1.2 | 31.8 | 38.16 | 10.3 | 6.7 | 17.4514 | YES | 1
13 | 1.2 | 31.8 | 38.16 | 9.8 | 6.6 | 17.4147 | YES | 1
14 | 1.2 | 31.8 | 38.16 | 9.1 | 6.5 | 17.6024 | YES | 1
15 | 1.2 | 31.8 | 38.16 | 10 | 6.5 | 16.6179 | YES | 1
16 | 1.2 | 31.8 | 38.16 | 9.8 | 6.6 | 17.4147 | YES | 1
17 | 1.2 | 31.8 | 38.16 | 9.1 | 6.5 | 17.6024 | YES | 1
18 | 1.2 | 31.8 | 38.16 | 9.7 | 6.5 | 16.9389 | YES | 1
19 | 1.2 | 31.8 | 38.16 | 9.1 | 6.6 | 18.2166 | YES | 1
20 | 1.2 | 31.8 | 38.16 | 7.1 | 6.5 | 20.0363 | YES | 1
21 | 1.2 | 31.8 | 38.16 | 7.3 | 6.6 | 20.4771 | YES | 1
22 | 1.2 | 31.8 | 38.16 | 7.7 | 6.5 | 19.2685 | YES | 1
23 | 1.2 | 31.8 | 38.16 | 6.7 | 6.6 | 21.299 | YES | 1
24 | 1.2 | 31.8 | 38.16 | 6.1 | 6.6 | 22.1578 | YES | 1
25 | 1 | 31.8 | 31.8 | 5.2 | 6.6 | 22.9902 | YES | 1
26 | 1 | 31.8 | 31.8 | 5.9 | 6.6 | 21.9504 | YES | 1
27 | 1 | 31.8 | 31.8 | 6 | 6.5 | 21.0551 | YES | 1
28 | 1.2 | 31.8 | 38.16 | 5.6 | 6.5 | 22.1097 | YES | 1
29 | 1.2 | 31.8 | 38.16 | 5.1 | 6.6 | 23.6753 | YES | 1
30 | 1.2 | 31.8 | 38.16 | 4.9 | 6.6 | 23.9923 | YES | 1
31 | 1.2 | 31.8 | 38.16 | 4.6 | 6.6 | 24.4766 | YES | 1
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
yes
yes
yes
yes
Calvin Napier