## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-06-05
System Name: | Coos Co Parks-LaVerne |  |  | ID#: 41 | 94557 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.04
2 |  |  | 0.04
3 |  |  | 0.04
4 |  |  | 0.04
5 |  |  | 0.04
6 |  |  | 0.04
7 |  |  | 0.04
8 |  |  | 0.04
9 |  |  | 0.04
10 |  |  | 0.04
11 |  |  | 0.04
12 |  |  | 0.04
13 |  |  | 0.04
14 |  |  | 0.04
15 |  |  | 0.04
16 |  |  | 0.04
17 |  |  | 0.04
18 |  |  | 0.04
19 |  |  | 0.04
20 |  |  | 0.04
21 |  |  | 0.04
22 |  |  | 0.04
23 |  |  | 0.04
24 |  |  | 0.04
25 |  |  | 0.04
26 |  |  | 0.04
27 |  |  | 0.03
28 |  |  | 0.04
29 |  |  | 0.04
30 |  |  | 0.04
31 |  |  | 0.04
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes:
[5 empty] | SIGNATURE: |  |  | 2024-06-05
[5 empty] | PHONE #: ( 541 )396-2344 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : B
System Name: | Coos Co. Parks Lav. |  | ID#: 41 | 94557 | Month/Year: 0523 | 2024-06-05 | Disinfection Giardia Log Inactiv: | 0.5 | ``````````````````
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow |  | ``````````````````````````````````````````````````````` | `````````````````````````````````````````````````````````````````````````````````````````````````````````
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 1.4 | 31.8 | 44.52 | 16.2 | 6.2 | 9.7531 | YES | 1
2 | 1.4 | 31.8 | 44.52 | 17.4 | 6.1 | 8.6574 | YES | 1
3 | 1.4 | 31.8 | 44.52 | 16.7 | 6.1 | 9.0794 | YES | 1
4 | 1.4 | 31.8 | 44.52 | 16.4 | 6.2 | 9.6218 | YES | 1
5 | 1.4 | 31.8 | 44.52 | 17.4 | 6.3 | 9.3361 | YES | 1
6 | 1.4 | 31.8 | 44.52 | 17.1 | 6.2 | 9.1757 | YES | 1
7 | 1.4 | 31.8 | 44.52 | 16.8 | 6.2 | 9.3644 | YES | 1
8 | 1.4 | 31.8 | 44.52 | 17.2 | 6.1 | 8.776 | YES | 1
9 | 1.2 | 31.8 | 38.16 | 18.3 | 6.1 | 7.9545 | YES | 1
10 | 1.4 | 31.8 | 44.52 | 17.7 | 6.1 | 8.4823 | YES | 1
11 | 1.3 | 31.8 | 41.34 | 17.7 | 6.1 | 8.3842 | YES | 1
12 | 1 | 31.8 | 31.8 | 18 | 6.1 | 7.932 | YES | 1
13 | 1 | 31.8 | 31.8 | 17.1 | 6.1 | 8.4344 | YES | 1
14 | 1 | 31.8 | 31.8 | 16.4 | 6 | 8.518 | YES | 1
15 | 1 | 31.8 | 31.8 | 16.1 | 6.1 | 9.0283 | YES | 1
16 | 1 | 31.8 | 31.8 | 15.8 | 6.2 | 9.5678 | YES | 1
17 | 1 | 31.8 | 31.8 | 15.7 | 6.1 | 9.2769 | YES | 1
18 | 1 | 31.8 | 31.8 | 16.1 | 6.1 | 9.0283 | YES | 1
19 | 1 | 31.8 | 31.8 | 16.9 | 6.4 | 9.5748 | YES | 1
20 | 0.8 | 31.8 | 25.44 | 17.2 | 6.3 | 8.8276 | YES | 1
21 | 0.8 | 31.8 | 25.44 | 17.3 | 6.3 | 8.7677 | YES | 1
22 | 0.8 | 31.8 | 25.44 | 16.6 | 6.2 | 8.8544 | YES | 1
23 | 0.8 | 31.8 | 25.44 | 17.1 | 6.1 | 8.2403 | YES | 1
24 | 1 | 31.8 | 31.8 | 20.1 | 6.1 | 6.8678 | YES | 1
25 | 1 | 31.8 | 31.8 | 19.1 | 6.1 | 7.3565 | YES | 1
26 | 1 | 31.8 | 31.8 | 20 | 6.1 | 6.9153 | YES | 1
27 | 0.8 | 31.8 | 25.44 | 21.3 | 6.3 | 6.6669 | YES | 1
28 | 0.8 | 31.8 | 25.44 | 20.2 | 6.2 | 6.9219 | YES | 1
29 | 0.8 | 31.8 | 25.44 | 21.3 | 6.1 | 6.1741 | YES | 1
30 | 0.8 | 31.8 | 25.44 | 21.2 | 6.3 | 6.7131 | YES | 1
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
yes
yes
yes
yes
Calvin Napier