## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-11-05
System Name: | Coos Co Parks-LaVerne |  |  | ID#: 41 | 94557 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.05
2 |  |  | 0.05
3 |  |  | 0.05
4 |  |  | 0.05
5 |  |  | 0.05
6 |  |  | 0.05
7 |  |  | 0.05
8 |  |  | 0.05
9 |  |  | 0.05
10 |  |  | 0.05
11 |  |  | 0.05
12 |  |  | 0.05
13 |  |  | 0.05
14 |  |  | 0.05
15 |  |  | 0.05
16 |  |  | 0.05
17 |  |  | 0.05
18 |  |  | 0.05
19 |  |  | 0.05
20 |  |  | 0.05
21 |  |  | 0.05
22 |  |  | 0.05
23 |  |  | 0.05
24 |  |  | 0.05
25 |  |  | 0.05
26 |  |  | 0.05
27 |  |  | 0.05
28 |  |  | 0.05
29 |  |  | 0.05
30 |  |  | 0.05
31
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes:
[5 empty] | SIGNATURE: |  |  | 2024-11-05
[5 empty] | PHONE #: ( 541 )396-2344 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : B
System Name: | Coos Co. Parks Lav. |  | ID#: 41 | 94557 | Month/Year: 0523 | 2024-11-05 | Disinfection Giardia Log Inactiv: | 0.5 | ``````````````````
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow |  | ``````````````````````````````````````````````````````` | `````````````````````````````````````````````````````````````````````````````````````````````````````````
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 0.8 | 31.8 | 25.44 | 12.8 | 6.2 | 11.4496 | YES | 1
2 | 1 | 31.8 | 31.8 | 12 | 6.2 | 12.993 | YES | 1
3 | 1 | 31.8 | 31.8 | 11.2 | 6.3 | 14.1042 | YES | 1
4 | 1.2 | 31.8 | 38.16 | 11.7 | 6.2 | 13.5151 | YES | 1
5 | 1.2 | 31.8 | 38.16 | 11.5 | 6.2 | 13.6827 | YES | 1
6 | 1.2 | 31.8 | 38.16 | 10.3 | 6.3 | 15.242 | YES | 1
7 | 1.2 | 31.8 | 38.16 | 10.8 | 6.2 | 14.289 | YES | 1
8 | 1.2 | 31.8 | 38.16 | 10.1 | 6.2 | 14.927 | YES | 1
9 | 1.2 | 31.8 | 38.16 | 11 | 6.3 | 14.5883 | YES | 1
10 | 1 | 31.8 | 31.8 | 11.6 | 6.2 | 13.3152 | YES | 1
11 | 1 | 31.8 | 31.8 | 11.2 | 6.2 | 13.6469 | YES | 1
12 | 1 | 31.8 | 31.8 | 11.7 | 6.3 | 13.6746 | YES | 1
13 | 1 | 31.8 | 31.8 | 12.2 | 6.2 | 12.8354 | YES | 1
14 | 1 | 31.8 | 31.8 | 11.2 | 6.1 | 13.2071 | YES | 1
15 | 1 | 31.8 | 31.8 | 10.5 | 6.2 | 14.2513 | YES | 1
16 | 1 | 31.8 | 31.8 | 10.9 | 6.1 | 13.4526 | YES | 1
17 | 1 | 31.8 | 31.8 | 11.1 | 6.2 | 13.7314 | YES | 1
18 | 1 | 31.8 | 31.8 | 10.2 | 6.2 | 14.5199 | YES | 1
19 | 0.8 | 31.8 | 25.44 | 9.9 | 6.2 | 14.4815 | YES | 1
20 | 0.8 | 31.8 | 25.44 | 9.1 | 6.1 | 14.725 | YES | 1
21 | 0.8 | 31.8 | 25.44 | 9.7 | 6.2 | 14.6633 | YES | 1
22 | 0.8 | 31.8 | 25.44 | 10.8 | 6.1 | 13.2538 | YES | 1
23 | 0.8 | 31.8 | 25.44 | 9.6 | 6.1 | 14.2731 | YES | 1
24 | 0.8 | 31.8 | 25.44 | 10.9 | 6.1 | 13.1728 | YES | 1
25 | 0.8 | 31.8 | 25.44 | 10.2 | 6.3 | 14.6935 | YES | 1
26 | 0.8 | 31.8 | 25.44 | 9.4 | 6.2 | 14.9411 | YES | 1
27 | 0.8 | 31.8 | 25.44 | 8.4 | 6.1 | 15.3859 | YES | 1
28 | 0.8 | 31.8 | 25.44 | 7.6 | 6.1 | 16.1837 | YES | 1
29 | 0.8 | 31.8 | 25.44 | 7.1 | 6.3 | 17.8868 | YES | 1
30 | 0.8 | 31.8 | 25.44 | 6.2 | 6.1 | 17.6972 | YES | 1
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
yes
yes
yes
yes
Calvin Napier