## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-05-01
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 30 | 30 | 0 | 30 | 0.034
2 | 30 | 30 | 0 | 30 | 0.03
3 | 30 | 30 | 0 | 30 | 0.03
4 | 30 | 30 | 0 | 30 | 0.03
5 | 40 | 40 | 0 | 30 | 0.03
6 | 30 | 30 | 0 | 30 | 0.03
7 | 40 | 40 | 0 | 30 | 0.03
8 | 30 | 30 | 0 | 30 | 0.03
9 | 30 | 30 | 0 | 30 | 0.03
10 | 40 | 40 | 0 | 30 | 0.03
11 | 30 | 30 | 0 | 30 | 0.03
12 | 30 | 30 | 0 | 30 | 0.03
13 | 40 | 40 | 0 | 30 | 0.03
14 | 35 | 35 | 0 | 30 | 0.03
15 | 35 | 35 | 0 | 30 | 0.03
16 | 35 | 35 | 0 | 30 | 0.03
17 | 35 | 35 | 0 | 30 | 0.03
18 | 35 | 35 | 0 | 30 | 0.03
19 | 35 | 35 | 0 | 30 | 0.03
20 | 30 | 30 | 0 | 30 | 0.03
21 | 30 | 30 | 0 | 30 | 0.03
22 | 40 | 40 | 0 | 30 | 0.03
23 | 30 | 30 | 0 | 30 | 0.03
24 | 30 | 30 | 0 | 30 | 0.03
25 | 30 | 30 | 0 | 30 | 0.037
26 | 40 | 40 | 0 | 30 | 0.03
27 | 40 | 40 | 0 | 30 | 0.03
28 | 30 | 30 | 0 | 30 | 0.04
29 | 30 | 30 | 0 | 30 | 0.03
30 | 30 | 30 | 0 | 30 | 0.03
31 | 30 | 30 | 0 | 30 | 0.03
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | yes
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Cal Napier |  | 5/312025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344 |  | sws-317697
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | COOS COUNTY PARK LAVERN |  | ID#: 41 | 94557 | 05/2025 |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 71 | 85.2 | 10.3 | 6.3 | 15.242 | YES | 7
2 | 1.2 | 71 | 85.2 | 11.1 | 6.3 | 14.4976 | YES | 7
3 | 1.2 | 71 | 85.2 | 12.3 | 6.2 | 13.0267 | YES | 7
4 | 1.2 | 71 | 85.2 | 12.4 | 6.6 | 14.7704 | YES | 7
5 | 1 | 71 | 71 | 10.3 | 6.6 | 16.5023 | YES | 7
6 | 1 | 71 | 71 | 11.8 | 6.7 | 15.5219 | YES | 7
7 | 1.2 | 71 | 85.2 | 15.1 | 6.2 | 10.2666 | YES | 7
8 | 2 | 71 | 142 | 12.3 | 6.4 | 15.1492 | YES | 7
9 | 2 | 71 | 142 | 11.4 | 6 | 14.0289 | YES | 7
10 | 1.8 | 71 | 127.8 | 14.4 | 6.1 | 11.1095 | YES | 7
11 | 1.8 | 71 | 127.8 | 14 | 6.5 | 13.2492 | YES | 7
12 | 1.4 | 71 | 99.4 | 13.9 | 6.7 | 13.7258 | YES | 7
13 | 1.8 | 71 | 127.8 | 14.2 | 6.5 | 13.0728 | YES | 7
14 | 1.8 | 71 | 127.8 | 14 | 6.4 | 12.765 | YES | 7
15 | 1.8 | 71 | 127.8 | 13.9 | 6.4 | 12.8509 | YES | 7
16 | 1.8 | 71 | 127.8 | 12.3 | 6.7 | 16.4006 | YES | 7
17 | 1.8 | 71 | 127.8 | 13.8 | 6.3 | 12.4642 | YES | 7
18 | 1.4 | 71 | 99.4 | 13.8 | 6.4 | 12.3578 | YES | 7
19 | 1.6 | 71 | 113.6 | 13.9 | 6.6 | 13.5307 | YES | 7
20 | 1.4 | 71 | 99.4 | 12.6 | 6.7 | 14.972 | YES | 7
21 | 1.4 | 71 | 99.4 | 12.3 | 6.7 | 15.7041 | YES | 7
22 | 1.4 | 71 | 99.4 | 13.8 | 6.4 | 12.3578 | YES | 7
23 | 1.4 | 71 | 99.4 | 12.9 | 6.3 | 12.6469 | YES | 7
24 | 1.4 | 71 | 99.4 | 13.2 | 6.4 | 12.8655 | YES | 7
25 | 1.4 | 71 | 99.4 | 13.1 | 6.3 | 12.4783 | YES | 7
26 | 1.4 | 71 | 99.4 | 14.9 | 6.4 | 11.4769 | YES | 7
27 | 1.4 | 71 | 99.4 | 14.7 | 6.4 | 11.6324 | YES | 7
28 | 1.4 | 71 | 99.4 | 13.8 | 6.5 | 12.827 | YES | 7
29 | 1.4 | 71 | 99.4 | 14 | 6.6 | 13.1363 | YES | 7
30 | 1.5 | 71 | 106.5 | 14.7 | 6.4 | 11.7668 | YES | 7
31 | 1.4 | 71 | 99.4 | 14.9 | 6.5 | 11.9138 | YES | 7
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2