## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-06-01
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 30 | 30 | 0 | 30 | 0.035
2 | 30 | 30 | 0 | 30 | 0.033
3 | 30 | 30 | 0 | 30 | 0.034
4 | 35 | 35 | 0 | 30 | 0.033
5 | 35 | 35 | 0 | 30 | 0.032
6 | 30 | 30 | 0 | 30 | 0.033
7 | 30 | 30 | 0 | 30 | 0.033
8 | 30 | 30 | 0 | 30 | 0.033
9 | 30 | 30 | 0 | 30 | 0.035
10 | 30 | 30 | 0 | 30 | 0.033
11 | 30 | 30 | 0 | 30 | 0.035
12 | 30 | 30 | 0 | 30 | 0.034
13 | 32 | 32 | 0 | 30 | 0.038
14 | 30 | 30 | 0 | 30 | 0.035
15 | 32 | 32 | 0 | 30 | 0.034
16 | 32 | 32 | 0 | 30 | 0.032
17 | 30 | 30 | 0 | 30 | 0.034
18 | 30 | 30 | 0 | 30 | 0.034
19 | 30 | 30 | 0 | 30 | 0.03
20 | 30 | 30 | 0 | 30 | 0.034
21 | 30 | 30 | 0 | 30 | 0.034
22 | 30 | 30 | 0 | 30 | 0.034
23 | 30 | 30 | 0 | 30 | 0.033
24 | 30 | 30 | 0 | 30 | 0.034
25 | 30 | 30 | 0 | 30 | 0.034
26 | 30 | 30 | 0 | 30 | 0.03
27 | 30 | 30 | 0 | 30 | 0.03
28 | 30 | 30 | 0 | 30 | 0.035
29 | 30 | 30 | 0 | 30 | 0.035
30 | 30 | 30 | 0 | 30 | 0.03
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | no | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Calvin Napier
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 07/14/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344 |  | SWS317697
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | COOS COUNTY PARK LAVERN |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.4 | 71 | 99.4 | 15.8 | 6.3 | 10.4041 | YES
2 | 1.4 | 71 | 99.4 | 16.1 | 6.2 | 9.8193 | YES
3 | 1.4 | 71 | 99.4 | 17.3 | 6.1 | 8.7165 | YES
4 | 1.4 | 71 | 99.4 | 17.5 | 6.2 | 8.9297 | YES
5 | 1.4 | 71 | 99.4 | 17.5 | 6.2 | 8.9297 | YES
6 | 1.4 | 71 | 99.4 | 17.5 | 6.4 | 9.6289 | YES
7 | 1.4 | 71 | 99.4 | 17.5 | 6.2 | 8.9297 | YES
8 | 1.5 | 71 | 106.5 | 21.1 | 6.2 | 7.064 | YES
9 | 1.4 | 71 | 99.4 | 22.1 | 6.4 | 7.0349 | YES
10 | 1.4 | 71 | 99.4 | 20.3 | 6.2 | 7.3759 | YES
11 | 1.4 | 71 | 99.4 | 18.6 | 6.4 | 8.9363 | YES
12 | 1.2 | 71 | 85.2 | 16.2 | 6.4 | 10.2741 | YES
13 | 0.8 | 71 | 56.8 | 16.2 | 6.5 | 10.1858 | YES
14 | 0.8 | 71 | 56.8 | 16 | 6.7 | 11.1279 | YES
15 | 0.8 | 71 | 56.8 | 16 | 6.7 | 11.1279 | YES
16 | 0.8 | 71 | 56.8 | 20.3 | 6.5 | 7.7074 | YES
17 | 0.8 | 71 | 56.8 | 21 | 6.5 | 7.3464 | YES
18 | 0.8 | 71 | 56.8 | 17.7 | 6.6 | 9.5549 | YES
19 | 0.7 | 71 | 49.7 | 18 | 6.7 | 9.6098 | YES
20 | 0.6 | 71 | 42.6 | 17.4 | 6.7 | 9.8932 | YES
21 | 0.8 | 71 | 56.8 | 16.7 | 6.8 | 11.02 | YES
22 | 0.8 | 71 | 56.8 | 16.8 | 6.7 | 10.5434 | YES
23 | 0.8 | 71 | 56.8 | 17 | 6.7 | 10.4019 | YES
24 | 0.8 | 71 | 56.8 | 16.7 | 6.6 | 10.224 | YES
25 | 0.8 | 71 | 56.8 | 18.1 | 6.7 | 9.656 | YES
26 | 0.6 | 71 | 42.6 | 19.4 | 6.6 | 8.3167 | YES
27 | 0.6 | 71 | 42.6 | 19.4 | 6.6 | 8.3167 | YES
28 | 0.6 | 71 | 42.6 | 19.2 | 6.6 | 8.4309 | YES
29 | 0.6 | 71 | 42.6 | 20.6 | 6.6 | 7.6621 | YES
30 | 0.6 | 71 | 42.6 | 21.3 | 6.7 | 7.5866 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2