## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-07-25
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 33 | 33 | 0 | 30 | 0.036
2 | 33 | 33 | 0 | 30 | 0.034
3 | 33 | 33 | 0 | 30 | 0.03
4 | 32 | 32 | 0 | 30 | 0.03
5 | 32 | 32 | 0 | 30 | 0.032
6 | 33 | 33 | 0 | 30 | 0.033
7 | 32 | 32 | 0 | 30 | 0.04
8 | 32 | 32 | 0 | 30 | 0.04
9 | 32 | 32 | 0 | 30 | 0.04
10 | 32 | 32 | 0 | 30 | 0.038
11 | 32 | 32 | 0 | 30 | 0.04
12 | 32 | 32 | 0 | 30 | 0.03
13 | 32 | 32 | 0 | 30 | 0.03
14 | 33 | 33 | 0 | 30 | 0.03
15 | 33 | 33 | 0 | 30 | 0.03
16 | 32 | 32 | 0 | 30 | 0.032
17 | 32 | 32 | 0 | 30 | 0.034
18 | 32 | 32 | 0 | 30 | 0.034
19 | 32 | 32 | 0 | 30 | 0.03
20 | 32 | 32 | 0 | 30 | 0.034
21 | 32 | 32 | 0 | 30 | 0.034
22 | 32 | 32 | 0 | 30 | 0.034
23 | 32 | 32 | 0 | 30 | 0.033
24 | 32 | 32 | 0 | 30 | 0.034
25 | 32 | 32 | 0 | 30 | 0.034
26 | 32 | 32 | 0 | 30 | 0.03
27 | 32 | 32 | 0 | 30 | 0.04
28 | 32 | 32 | 0 | 30 | 0.03
29 | 32 | 32 | 0 | 30 | 0.03
30 | 32 | 32 | 0 | 30 | 0.03
31 | 32 | 32 | 0 | 30 | 0.03
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Calvin Napier
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 07/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Coos Co PKS LaVerne |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 104 | 52 | 20.1 | 6.7 | 8.1397 | YES
2 | 0.5 | 104 | 52 | 21.2 | 6.6 | 7.2677 | YES
3 | 0.5 | 104 | 52 | 21.7 | 6.7 | 7.2954 | YES
4 | 0.5 | 104 | 52 | 20 | 6.7 | 8.1954 | YES
5 | 0.6 | 104 | 62.4 | 19.1 | 6.4 | 7.8688 | YES
6 | 0.6 | 104 | 62.4 | 18.6 | 6.7 | 9.1203 | YES
7 | 0.8 | 104 | 83.2 | 19.5 | 6.9 | 9.4686 | YES
8 | 0.8 | 104 | 83.2 | 20.5 | 6.8 | 8.5188 | YES
9 | 0.8 | 104 | 83.2 | 21.3 | 6.6 | 7.4762 | YES
10 | 0.5 | 104 | 52 | 21.1 | 6.8 | 7.8962 | YES
11 | 0.5 | 104 | 52 | 20.4 | 6.8 | 8.2828 | YES
12 | 0.6 | 104 | 62.4 | 21.5 | 6.7 | 7.4833 | YES
13 | 0.6 | 104 | 62.4 | 21.9 | 6.8 | 7.5634 | YES
14 | 0.6 | 104 | 62.4 | 22.3 | 6.7 | 7.0834 | YES
15 | 0.5 | 104 | 52 | 21.6 | 6.8 | 7.6307 | YES
16 | 0.5 | 104 | 52 | 20.4 | 7 | 8.9335 | YES
17 | 0.5 | 104 | 52 | 23.2 | 7.1 | 7.6653 | YES
18 | 0.5 | 104 | 52 | 20.2 | 7 | 9.0557 | YES
19 | 0.6 | 104 | 62.4 | 20 | 7.1 | 9.6429 | YES
20 | 0.6 | 104 | 62.4 | 20.4 | 6.9 | 8.7028 | YES
21 | 0.6 | 104 | 62.4 | 20.5 | 6.8 | 8.3229 | YES
22 | 0.6 | 104 | 62.4 | 18.9 | 7 | 10.0051 | YES
23 | 0.6 | 104 | 62.4 | 20.4 | 7.1 | 9.385 | YES
24 | 0.6 | 104 | 62.4 | 20.5 | 6.9 | 8.6438 | YES
25 | 0.6 | 104 | 62.4 | 20.5 | 6.8 | 8.3229 | YES
26 | 0.6 | 104 | 62.4 | 20.3 | 6.9 | 8.7622 | YES
27 | 0.6 | 104 | 62.4 | 19.4 | 6.4 | 7.709 | YES
28 | 1 | 104 | 104 | 19 | 6.7 | 9.2972 | YES
29 | 1 | 104 | 104 | 19.2 | 7 | 10.2676 | YES
30 | 1 | 104 | 104 | 19.5 | 6.7 | 8.9869 | YES
31 | 1 | 104 | 104 | 19.7 | 7 | 9.9263 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2