## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-09-01
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 19.5 | 19.5 | 0 | 30 | 0.039
2 | 23 | 23 | 0 | 30 | 0.034
3 | 20 | 20 | 0 | 30 | 0.029
4 | 20 | 20 | 0 | 30 | 0.021
5 | 20 | 20 | 0 | 30 | 0.022
6 | 20 | 20 | 0 | 30 | 0.03
7 | 17 | 17 | 0 | 30 | 0.027
8 | 16 | 16 | 0 | 30 | 0.027
9 | 20 | 20 | 0 | 30 | 0.039
10 | 20 | 20 | 0 | 30 | 0.033
11 | 16 | 16 | 0 | 30 | 0.033
12 | 18 | 18 | 0 | 30 | 0.03
13 | 20 | 20 | 0 | 30 | 0.03
14 | 19 | 19 | 0 | 30 | 0.034
15 | 20 | 20 | 0 | 30 | 0.035
16 | 28 | 28 | 0 | 30 | 0.035
17 | 30 | 30 | 0 | 30 | 0.038
18 | 25 | 25 | 0 | 30 | 0.04
19 | 26 | 26 | 0 | 30 | 0.04
20 | 20 | 20 | 0 | 30 | 0.04
21 | 20 | 20 | 0 | 30 | 0.04
22 | 26 | 26 | 0 | 30 | 0.05
23 | 20 | 20 | 0 | 30 | 0.05
24 | 20 | 20 | 0 | 30 | 0.05
25 | 30 | 30 | 0 | 30 | 0.05
26 | 30 | 30 | 0 | 30 | 0.05
27 | 30 | 30 | 0 | 30 | 0.05
28 | 34 | 34 | 0 | 30 | 0.05
29 | 31 | 31 | 0 | 30 | 0.05
30 | 28 | 28 | 0 | 30 | 0.06
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Caden Thurman
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 09/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Coos Co PKS LaVerne |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 104 | 83.2 | 21.5 | 7.1 | 8.9139 | YES
2 | 0.9 | 104 | 93.6 | 19.3 | 7.3 | 11.2812 | YES
3 | 0.8 | 104 | 83.2 | 20 | 7.4 | 11.044 | YES
4 | 0.7 | 104 | 72.8 | 21.2 | 7.4 | 10.0678 | YES
5 | 0.8 | 104 | 83.2 | 20.5 | 7.4 | 10.6778 | YES
6 | 0.8 | 104 | 83.2 | 20.3 | 7.5 | 11.2357 | YES
7 | 0.7 | 104 | 72.8 | 19.1 | 7.5 | 12.0413 | YES
8 | 0.8 | 104 | 83.2 | 19.8 | 7.5 | 11.6203 | YES
9 | 0.7 | 104 | 72.8 | 19.8 | 7.3 | 10.659 | YES
10 | 0.7 | 104 | 72.8 | 20.1 | 7.5 | 11.2579 | YES
11 | 0.6 | 104 | 62.4 | 19.3 | 7.3 | 10.8984 | YES
12 | 0.5 | 104 | 52 | 19 | 7.4 | 11.4129 | YES
13 | 0.7 | 104 | 72.8 | 19.2 | 7.8 | 13.3754 | YES
14 | 0.4 | 104 | 41.6 | 19.9 | 7.6 | 11.4436 | YES
15 | 0.7 | 104 | 72.8 | 18 | 7.5 | 12.9641 | YES
16 | 0.6 | 104 | 62.4 | 18.1 | 7.4 | 12.2649 | YES
17 | 0.5 | 104 | 52 | 19.3 | 7.3 | 10.7736 | YES
18 | 0.4 | 104 | 41.6 | 19.8 | 7.8 | 12.4141 | YES
19 | 0.5 | 104 | 52 | 19.7 | 7.6 | 11.7327 | YES
20 | 0.6 | 104 | 62.4 | 20.1 | 7.4 | 10.72 | YES
21 | 0.5 | 104 | 52 | 18.7 | 7.6 | 12.5481 | YES
22 | 0.6 | 104 | 62.4 | 17.1 | 7.4 | 13.116 | YES
23 | 0.8 | 104 | 83.2 | 17.1 | 7.4 | 13.4196 | YES
24 | 0.8 | 104 | 83.2 | 17.8 | 7.3 | 12.3361 | YES
25 | 0.8 | 104 | 83.2 | 17.8 | 7.5 | 13.2902 | YES
26 | 0.6 | 104 | 62.4 | 20.8 | 7.01 | 8.8286 | YES
27 | 0.6 | 104 | 62.4 | 19.3 | 6.67 | 8.5984 | YES
28 | 0.6 | 104 | 62.4 | 17.1 | 7.6 | 14.1286 | YES
29 | 0.7 | 104 | 72.8 | 18 | 7.4 | 12.4899 | YES
30 | 0.7 | 104 | 72.8 | 16.5 | 7.5 | 14.3335 | YES
31 |  | 104
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2