## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-10-25
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 30 | 30 | 0 | 30 | 0.054
2 | 30 | 30 | 0 | 30 | 0.05
3 | 30 | 30 | 0 | 30 | 0.06
4 | 30 | 30 | 0 | 30 | 0.06
5 | 30 | 30 | 0 | 30 | 0.06
6 | 30 | 30 | 0 | 30 | 0.06
7 | 30 | 30 | 0 | 30 | 0.06
8 | 30 | 30 | 0 | 30 | 0.06
9 | 30 | 30 | 0 | 30 | 0.06
10 | 30 | 30 | 0 | 30 | 0.06
11 | 30 | 30 | 0 | 30 | 0.06
12 | 30 | 30 | 0 | 30 | 0.06
13 | 30 | 30 | 0 | 30 | 0.06
14 | 30 | 30 | 0 | 30 | 0.06
15 | 30 | 30 | 0 | 30 | 0.07
16 | 30 | 30 | 0 | 30 | 0.06
17 | 30 | 30 | 0 | 30 | 0.06
18 | 30 | 30 | 0 | 30 | 0.07
19 | 30 | 30 | 0 | 30 | 0.06
20 | 30 | 30 | 0 | 30 | 0.06
21 | 30 | 30 | 0 | 30 | 0.06
22 | 30 | 30 | 0 | 30 | 0.06
23 | 30 | 30 | 0 | 30 | 0.07
24 | 30 | 30 | 0 | 30 | 0.06
25 | 30 | 30 | 0 | 30 | 0.06
26 | 30 | 30 | 0 | 30 | 0.06
27 | 30 | 30 | 0 | 30 | 0.06
28 | 30 | 30 | 0 | 30 | 0.07
29 | 30 | 30 | 0 | 30 | 0.07
30 | 30 | 30 | 0 | 30 | 0.06
31 | 30 | 30 | 0 | 30 | 0.06
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Caden Thurman
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 10/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Coos Co PKS LaVerne |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 104 | 62.4 | 19.3 | 7.01 | 9.7745 | YES
2 | 0.6 | 104 | 62.4 | 18.8 | 7.08 | 10.3801 | YES
3 | 0.6 | 104 | 62.4 | 16.7 | 7.06 | 11.869 | YES
4 | 0.6 | 104 | 62.4 | 16.1 | 7.02 | 12.1742 | YES
5 | 0.8 | 104 | 83.2 | 16.3 | 7.03 | 12.3365 | YES
6 | 0.8 | 104 | 83.2 | 19.9 | 7.03 | 9.6775 | YES
7 | 0.8 | 104 | 83.2 | 19.3 | 7.03 | 10.0786 | YES
8 | 0.8 | 104 | 83.2 | 20.1 | 7.05 | 9.6193 | YES
9 | 0.8 | 104 | 83.2 | 19.7 | 7.03 | 9.8094 | YES
10 | 0.8 | 104 | 83.2 | 18.6 | 7.11 | 10.8883 | YES
11 | 1.2 | 104 | 124.8 | 18.9 | 7.17 | 11.4267 | YES
12 | 0.8 | 104 | 83.2 | 19.6 | 7.17 | 10.4092 | YES
13 | 0.8 | 104 | 83.2 | 18.5 | 7.45 | 12.4468 | YES
14 | 0.8 | 104 | 83.2 | 17.8 | 7.42 | 12.9003 | YES
15 | 0.8 | 104 | 83.2 | 17 | 7.45 | 13.7633 | YES
16 | 0.9 | 104 | 93.6 | 16.8 | 7.04 | 12.1117 | YES
17 | 0.8 | 104 | 83.2 | 11.6 | 6.93 | 16.6247 | YES
18 | 0.8 | 104 | 83.2 | 17.4 | 7.05 | 11.543 | YES
19 | 0.8 | 104 | 83.2 | 17.1 | 7.03 | 11.6907 | YES
20 | 0.8 | 104 | 83.2 | 15.5 | 7.032 | 13.0264 | YES
21 | 0.6 | 104 | 62.4 | 11 | 7.32 | 19.3214 | YES
22 | 0.6 | 104 | 62.4 | 11.2 | 7.63 | 21.2448 | YES
23 | 0.6 | 104 | 62.4 | 12.8 | 7.73 | 19.7399 | YES
24 | 0.6 | 104 | 62.4 | 12.4 | 7.52 | 18.9067 | YES
25 | 0.6 | 104 | 62.4 | 13.7 | 7.6 | 17.7238 | YES
26 | 0.7 | 104 | 72.8 | 16.8 | 7.11 | 12.1502 | YES
27 | 0.6 | 104 | 62.4 | 11.1 | 7.5 | 20.4349 | YES
28 | 0.6 | 104 | 62.4 | 11.6 | 7.5 | 19.7784 | YES
29 | 0.6 | 104 | 62.4 | 13.1 | 7.5 | 17.7765 | YES
30 | 0.7 | 104 | 72.8 | 11.3 | 7.6 | 21.1215 | YES
31 | 0.7 | 104 | 72.8 | 12.8 | 7.6 | 19.0308 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2