## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-11-25
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 30 | 30 | 0 | 30 | 0.073
2 | 30 | 30 | 0 | 30 | 0.069
3 | 30 | 30 | 0 | 30 | 0.065
4 | 30 | 30 | 0 | 30 | 0.071
5 | 30 | 30 | 0 | 30 | 0.069
6 | 30 | 30 | 0 | 30 | 0.068
7 | 30 | 30 | 0 | 30 | 0.024
8 | 30 | 30 | 0 | 30 | 0.023
9 | 30 | 30 | 0 | 30 | 0.03
10 | 30 | 30 | 0 | 30 | 0.022
11 | 30 | 30 | 0 | 30 | 0.03
12 | 30 | 30 | 0 | 30 | 0.02
13 | 30 | 30 | 0 | 30 | 0.02
14 | 30 | 30 | 0 | 30 | 0.01
15 | 30 | 30 | 0 | 30 | 0.01
16 | 30 | 30 | 0 | 30 | 0.01
17 | 30 | 30 | 0 | 30 | 0.01
18 | 40 | 40 | 0 | 30 | 0.01
19 | 40 | 40 | 0 | 30 | 0.01
20 | 40 | 40 | 0 | 30 | 0.01
21 | 40 | 40 | 0 | 30 | 0.01
22 | 40 | 40 | 0 | 30 | 0.02
23 | 40 | 40 | 0 | 30 | 0.02
24 | 40 | 40 | 0 | 30 | 0.02
25 | 40 | 40 | 0 | 30 | 0.02
26 | 40 | 40 | 0 | 30 | 0.01
27 | 40 | 40 | 0 | 30 | 0.02
28 | 40 | 40 | 0 | 30 | 0.02
29 | 40 | 40 | 0 | 30 | 0.02
30 | 40 | 40 | 0 | 30 | 0.01
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Caden Thurman
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 11/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Coos Co PKS LaVerne |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 104 | 72.8 | 13.1 | 7.5 | 17.9795 | YES
2 | 0.7 | 104 | 72.8 | 13.6 | 7.4 | 16.7604 | YES
3 | 0.6 | 104 | 62.4 | 12.5 | 7.06 | 15.7228 | YES
4 | 0.4 | 104 | 41.6 | 13 | 7.43 | 17.0465 | YES
5 | 0.8 | 104 | 83.2 | 12.8 | 7.55 | 18.8961 | YES
6 | 1 | 104 | 104 | 12.5 | 7.23 | 17.5224 | YES
7 | 0.9 | 104 | 93.6 | 13.8 | 7.13 | 15.3099 | YES
8 | 0.8 | 104 | 83.2 | 12.5 | 7.43 | 18.4417 | YES
9 | 0.9 | 104 | 93.6 | 11.7 | 7.25 | 18.6332 | YES
10 | 1 | 104 | 104 | 11.7 | 7.26 | 18.9061 | YES
11 | 1.1 | 104 | 114.4 | 13.1 | 7.34 | 17.7354 | YES
12 | 1.2 | 104 | 124.8 | 13.4 | 7.15 | 16.391 | YES
13 | 1.2 | 104 | 124.8 | 13.6 | 7.15 | 16.174 | YES
14 | 1.2 | 104 | 124.8 | 12.6 | 7.24 | 17.872 | YES
15 | 1.3 | 104 | 135.2 | 12.4 | 7.32 | 19.0704 | YES
16 | 1 | 104 | 104 | 12.8 | 7.4 | 18.2891 | YES
17 | 0.8 | 104 | 83.2 | 12.5 | 7.13 | 16.507 | YES
18 | 0.8 | 104 | 83.2 | 11.7 | 7.34 | 19.0091 | YES
19 | 1.2 | 104 | 124.8 | 8 | 7.13 | 23.5564 | YES
20 | 0.8 | 104 | 83.2 | 10.3 | 7.23 | 20.043 | YES
21 | 0.8 | 104 | 83.2 | 9.3 | 7.32 | 22.0874 | YES
22 | 0.8 | 104 | 83.2 | 8.2 | 7.63 | 26.5301 | YES
23 | 0.8 | 104 | 83.2 | 9.2 | 7.73 | 25.7117 | YES
24 | 0.8 | 104 | 83.2 | 9.4 | 7.52 | 23.5459 | YES
25 | 0.8 | 104 | 83.2 | 8.7 | 7.6 | 25.3821 | YES
26 | 0.8 | 104 | 83.2 | 9.5 | 7.11 | 20.2543 | YES
27 | 0.8 | 104 | 83.2 | 9.8 | 7.5 | 22.768 | YES
28 | 0.8 | 104 | 83.2 | 9.9 | 7.5 | 22.6178 | YES
29 | 0.8 | 104 | 83.2 | 9.7 | 7.5 | 22.9193 | YES
30 | 0.8 | 104 | 83.2 | 9.8 | 7.6 | 23.5871 | YES
31 |  | 104 |  | 12.8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2